## Intro - Table List
2014 CBSA Full DB Data Dictionary This data dictionary provides details on each of the variables found in the 2014 CBSA Database. Each table of data found in the database is separated into its own tab in this file. Each tab contains the FACT database variable name, the associated survey question, a detailed description of each variable, and a definition of each coded value assigned to that variable. Below is a brief description of each data table and the associated tab name.
Table Name | Tab Name | Table Description
Case_Weights | Case Weights | Site regional case weights
Building_Information | Building Info | General Building Information
Building_Renovation_History | Renovation | History of renovations on the building and future renovation plans
Mixed_Use | Mixed Use | Identifies if a building is mixed use and gives information on the mixed use
General_Space_Information | Spaces | Identifies and defines the major different spaces of a building
Schedule | Schedule | Building Schedule identification
Hours | Hours | Hours for the identified schedule from the Schedule table (relational)
Energy_Sources | Energy Sources | Identifies all the energy sources used on site
Electric_Meters | Electric Meters | Additional information on the electric meter
Gas_Meters | Gas Meters | Additional information on the gas meter
Onsite_Generation | Generation | Characterizes any on-site power generation
Walls | Walls | Provides information on the building walls
Windows | Windows | Provides information on the building window(s)
Roofs | Roofs | Provides information on the building roof(s)
Floors | Floors | Provides information on the building floor(s)
HVAC_Summary | HVAC Summary | Provides an overall description of the building's HVAC description
Single_Zone_HVAC | SZ HVAC | Characterizes any Single Zone HVAC Systems onsite
Multi_Zone_HVAC | MZ HVAC | Characterizes any Multi Zone HVAC Systems onsite
Boilers | Boilers | Characterizes any boilers found onsite
Chillers | Chillers | Characterizes any chillers found onsite
Building_Controls | Building Controls | Provides detailed information on the building HVAC Controls
Water_Heaters | Water Heat | Characterizes any Water Heaters or Dedicated DHW Boilers onsite
Indoor_Outdoor_Fixture_Schedule | Light Schedule | Lists all of the indoor and outdoor fixtures onsite
Lighting_Summary | Light Summary | Describes the building lighting system
Indoor_Lighting | Indoor Lights | Identifies the Lighting Spaces, Subspaces and the sampled/total area of these subspaces
Indoor_Fixture_Takeoff | Fixture Takeoff | Lists all of the indoor lighting fixtures (defined in Light Schedule table) associated with each subspace area identified in Indoor Lighting table (relational)
Indoor_Fixture_Controls | Fixture Controls | Details the lighting controls for each of the lighting fixtures identified in Fixture Takeoff table (relational)
Outdoor_Lighting | Outdoor Lights | Lists all of the outdoor lighting fixtures (defined in Light Schedule table
Food_Service_Equipment | Food Equip | Provides information on Kitchens, Food Service Equipment, and Plug Load Refrigerators
Miscellaneous_Equipment | Misc. Equip | Provides information on Pools, Spas, Laundry and Laboratory equipment
Economic_Use_Equipment | Econ Misc. Equip | Provides information on miscellaneous equipment for all buildings and by economic use
Refrigeration_Compressors | Compressors | Characterizes the Refrigeration Compressors onsite
Refrigeration_Condensers | Condensers | Characterizes the Refrigeration Condensers onsite
Refrigerated_Display_Cases | Display Cases | Details all Refrigerated Display Cases onsite - these are defined as: • Self-contained or multiplex display systems accessible by customers (no stocking areas behind) • Includes open coffin cases
Refrigerated_Walkins_Storage_Boxes | Walk-ins | Details all Refrigerated Walk-ins/Storage Boxes onsite • Walk-ins are accessible by customers (refrigerated produce and beer walk-in-rooms) • Storage boxes do not have customer access
Refrigerated_Reach_ins | Reach-ins | Details all Refrigerated Reach-ins onsite • Display case systems with doors and employee accessed stocking or walk-in areas behind
Servers_Data_Centers | Servers | Provides information on the server rooms and equipment onsite
Residential_Areas | Residential Areas | Details residential areas within a commercial building
H&U Table Name | Tab Name | Hospitals and Universities Table Descriptions
HU_Space_Information | H&U Space Info | Provides data on the different space types of Hospitals and Universities only
HU_HVAC | H&U HVAC | Provides HVAC data for Hospitals and Universities only
HU_Lighting | H&U Lighting | Provides detailed lighting data for Hospitals and Universities only
HU_Miscellaneous | H&U Misc. | Details additional miscellaneous data specific to Hospitals and Universities

## Case Weights
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
site_id | NA | Unique site ID | NA
building_type | NA | Site building type | NA
size_bt | NA | Site size group (building type-specific) | NA
vintage | NA | Site vintage group | NA
urban | NA | Site urban/rural designation | NA
sfpnw | NA | Regional square footage represented by the site | NA

## Building Info
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
tbl_index |  | Building Info Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
bldg_condition | Is the site building primarily: Functional Demolished Vacant Inaccessible | Indicates the building condition or status. Either Functional, Demolished, Vacant, or Inaccessible | F = Functional D = Demolished V = Vacant I = Inaccessible
single_multiple | Is this site a Single building or a Multiple building Complex | Indicates whether the site is contained in a single building or multiple buildings (e.g., school with multiple buildings). | S = Single M = Multiple
building_num | If the site is part of a Multiple building complex, how many buildings are in the complex? | Indicates the number of buildings in a multiple building complex. (0 for Single Buildings)
primary_econ | What best describes the primary economic use of the building/complex? | Indicates the primary economic use of the building/complex from the Primary Economic Use. If the building type chosen is “’12. Other,”’ describe the building. | 1.) Assembly 2.) Grocery 3.) Retail/Service 4.) Hospital 5.) Lodging 6.) Residential Care 7.) Office 8.) Restaurant 9.) School K-12 10.) University 11.) Warehouse 12.) Other 13.) Unsampled
primary_econ_other | If Other, Describe: | If the building type cannot be classified by the Primary Economic Use Table, describe the building.
detailed_econ | What best describes the detailed economic use of the building/complex? | Indicate the detailed economic use of the building/complex from the Detailed Building Type Codes Table (see table below). | Table Below
detailed_econ_other | If Other, Describe: | If the building’s detailed economic use cannot be classified from the Detailed Building Type Codes Table, describe the building.
first_floor_perimeter | First floor perimeter (FT) | First floor perimeter of the surveyed building.
upper_floor_perimeter | Typical upper floor perimeter (FT) | Typical upper floor perimeter of the surveyed building.
floor_to_floor_height | Floor to floor height (FT) | Average or typical floor to floor height for the surveyed building. Use floor to roof/ceiling insulation height in 1 story buildings, and use average floor to floor height in buildings < 5 floors with very different first floors.
outdoor_park_spaces | If dedicated outdoor parking lot spaces with exterior lighting (# of spaces) | Number of dedicated outdoor parking spaces for the surveyed building/complex serviced by outdoor lighting fixtures that are fed through the building meter. This parameter may be estimated. Entered zero if none, -1 if # of parking space fed by building meter unknown.
heating_fuel | Primary Heating Fuel | Indicate the primary heating fuel of the building/complex from the Fuel Type Codes Table. In buildings with multi-zone systems with reheat, the reheat fuel should be considered primary. In buildings with heat pump loops, electric is the primary fuel. | 1.) Electricity 2.) Natural Gas 3.) Oil 4.) Propane 5.) Purchased Steam 6.) Purchased Hot Water 7.) Other 0.) None
heating_fuel_other |  | Filled if heating fuel type is 7 - Other
cooling_fuel | Primary Cooling Fuel | Indicate the primary cooling fuel of the building/complex from the Fuel Type Codes | 1.) Electricity 2.) Natural Gas 3.) Oil 4.) Propane 5.) Purchased Steam 6.) Purchased Hot Water 7.) Other 0.) None
cooling_fuel_other |  | Filled if cooling fuel type is 7 - Other
photos_bldg_exposure | Photos taken of each building exposure | Surveyors were asked take digital photos of each building/complex exposure and any unusual items or items requiring additional clarification.
has_servers | Are there areas within bldg. dedicated to holding computer servers? | If yes, server table should be filled
build_comments | Additional comments: | Capture any additional context that will help inform the interview responses for the above questions. Also, capture any other changes mentioned that could impact energy use (e.g. additional floor area being added in the next 2 years)
owner_occ_percent | What percentage of the building/complex is occupied by the Owner and/or Tenants? | What percentage of the building/complex is occupied by the owner of the building (% owner), and what percentage of the building/complex is occupied by a tenant (% tenant). An example of an owner occupied building would be a family-owned convenience store. An example of a tenant occupied building would be a multi-story office building with lower level retail.
tenant_occ_percent
tenant_number | Number of tenants currently in space | Approximate number of tenants that occupy the building/complex being audited. Do not include the owner.
energy_staff | Is there a staff person whose duties include energy conservation and/or management? | Applicable energy conservation and/or management staff would be a facilities engineer managing EMS controls, conservation program lead, etc. (Y/N)
percent_facade_lit | % façade Lit? | Percentage of the exterior building façade that is lit
detailed_econ variable
| Detailed Economic Use Description | Associated Primary Economic Use
1 | ARENA | Assembly
2 | AUDITORIUM | Assembly
3 | BOAT SLIPS, MARINA, YACHT CLUB | Assembly
4 | BOWLING ALLEY | Assembly
5 | CASINO | Assembly
6 | CLUB, LODGES | Assembly
7 | COMMUNITY CENTER | Assembly
8 | CONVENTION CENTER | Assembly
9 | GYM, EXERCISE | Assembly
10 | HEALTH SPA | Assembly
11 | ICE SKATING | Assembly
12 | LIBRARY | Assembly
13 | MUSEUM | Assembly
14 | MOVIE THEATER | Assembly
15 | PERFORMING ARTS THEATER | Assembly
16 | POOL | Assembly
17 | RECREATION CENTER | Assembly
18 | RELIGIOUS ASSEMBLY | Assembly
19 | ROLLER SKATING | Assembly
20 | SENIOR CENTER | Assembly
21 | OTHER ASSEMBLY | Assembly
22 | CONVENIENCE STORE (<=5,000SF) | Grocery
23 | GROCERY (> 5000SF) | Grocery
24 | GAS STATION WITH A CONVENIENCE STORE | Grocery
25 | OTHER GROCERY | Grocery
26 | AUTO PARTS | Retail
27 | AUTO/BOAT DEALER/ SHOWRM | Retail
28 | BEAUTY / BARBER | Retail
29 | BEER, WINE, OR LIQUOR STORE | Retail
30 | CAR WASH | Retail
31 | CLOTHING | Retail
32 | DEPARTMENT STORE | Retail
33 | DEPT. STORE W/ GROCERY | Retail
34 | DRY CLEANER | Retail
35 | ELECRONICS/APPLIANCES | Retail
36 | FLORIST, NURSERY | Retail
37 | HARDWARE | Retail
38 | HOME IMPROVEMENT | Retail
39 | LAUNDROMAT (SELF-SERVICE) | Retail
40 | PHARMACY | Retail
41 | POST OFFICE | Retail
42 | RENTAL CENTER | Retail
43 | REPAIR SHOP | Retail
44 | STUDIO/GALLERY | Retail
45 | VEHICLE REPAIR | Retail
46 | WAREHOUSE CLUB | Retail
47 | OTHER SPECIALTY MERCHANDISE | Retail
48 | HOSPITAL | Hospital
49 | HOTEL | Lodging
50 | MOTEL | Lodging
51 | BED & BREAKFAST | Lodging
52 | BOARDING/ROOMING HOUSE, APT HOTEL | Lodging
53 | CONVENT OR MONASTERY | Lodging
54 | DORMITORY | Lodging
55 | FRATERNITY, OR SORORITY | Lodging
56 | HALFWAY HOUSE | Lodging
57 | HOTEL - RESORT | Lodging
58 | SHELTER, ORPHANAGE, OR CHILDRENS HOME | Lodging
59 | OTHER LODGING | Lodging
60 | ASSISTED LIVING | Residential Care
61 | IN-PATIENT REHAB | Residential Care
62 | NURSING HOME | Residential Care
63 | RETIREMENT HOME | Residential Care
64 | OTHER RESIDENTIAL CARE | Residential Care
65 | OFFICE- ADMIN, PROFESSIONAL, GOVERNMENT, FINANCIAL | Office
66 | CALL CENTER | Office
67 | CITY HALL | Office
68 | DENTAL OFFICE | Office
69 | MEDICAL CLINIC / OUTPATIENT MEDICAL | Office
70 | MEDICAL OFFICE | Office
71 | MEDICAL URGENT CARE CLINIC | Office
72 | OUTPATIENT REHAB | Office
73 | RETAIL BANKING | Office
74 | SALES OFFICE | Office
75 | VETERINARIAN OFFICE/CLINIC | Office
76 | OTHER OFFICE | Office
77 | BAR, PUB, LOUNGE | Restaurant
78 | CAFETERIA | Restaurant
79 | CATERING SERVICE | Restaurant
80 | COFFEE, DOUGHNUT, OR BAGEL SHOP | Restaurant
81 | FAST FOOD RESTAURANT | Restaurant
82 | ICE CREAM OR FROZEN YOGURT SHOP | Restaurant
83 | SIT DOWN RESTAURANT | Restaurant
84 | TAKE-OUT RESTAURANT | Restaurant
85 | TRUCK STOP | Restaurant
86 | OTHER RESTAURANT | Restaurant
87 | ELEMENTARY SCHOOL | School
88 | MIDDLE SCHOOL | School
89 | HIGH SCHOOL | School
90 | PRE-SCHOOL | School
91 | OTHER K-12 SCHOOL | School
92 | UNIVERSITY / COLLEGE | University
93 | MINISTORAGE | Warehouse
94 | WAREHOUSE, DISTRIBUTION | Warehouse
95 | WAREHOUSE, STORAGE | Warehouse
96 | COLD STORAGE, NON-AMMONIA BASE REFG | Warehouse
97 | OTHER WAREHOUSE | Warehouse
98 | ADULT/CAREER EDUCATION | Other
99 | AIRPLANE HANGER | Other
100 | ASYLUM | Other
101 | COURTHOUSE | Other
102 | CREMATORIUM | Other
103 | DATA CENTER OR SERVER FARM | Other
104 | FIRE STATION | Other
105 | JAIL | Other
106 | POLICE STATION | Other
107 | POLICE & FIRE | Other
108 | PRISON | Other
109 | TELEPHONE SWITCHING | Other
110 | VOCATIONAL TRAINING | Other
111 | OTHER | Other
200 | AGRICULTURE | Unsampled
300 | INDUSTRIAL | Unsampled
301 | COLD STORAGE, AMMONIA | Unsampled
400 | MANUFACTURING | Unsampled
500 | RESIDENTIAL | Unsampled

## Renovation History
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
history_index |  | History Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
ballast_repl_ren | Were any of the Lighting Ballasts ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Lighting Ballasts
fixture_repl_ren | Were any of the Lighting Fixtures ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Lighting Fixtures
control_repl_ren | Were any of the Lighting Controls ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Lighting Controls
hvac_repl_ren | Were any of the HVAC Systems ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the HVAC Systems
hvac_control_repl_ren | Were any of the HVAC Controls ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the HVAC Controls
refer_repl_ren | Were any of the Refrigeration Systems ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Refrigeration Equipment
window_repl_ren | Were any of the Windows ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Windows
roof_ins_repl_ren | Was the Roof Insulation ever replaced or renovated? | Yes/No/Unknown if major renovations or replacements took place on the Roof Insulation
ballast_years_ago | Number of years ago that the Lighting Ballasts were renovated or replaced (if applicable) | Number of years ago that the Lighting Ballasts were renovated or replaced (if applicable)
fixture_years_ago | Number of years ago that the Lighting Fixtures were renovated or replaced (if applicable) | Number of years ago that the Lighting Fixtures were renovated or replaced (if applicable)
control_years_ago | Number of years ago that the Lighting Controls were renovated or replaced (if applicable) | Number of years ago that the Lighting Controls were renovated or replaced (if applicable)
hvac_years_ago | Number of years ago that the HVAC Systems were renovated or replaced (if applicable) | Number of years ago that the HVAC Systems were renovated or replaced (if applicable)
hvac_control_years_ago | Number of years ago that the HVAC Controls were renovated or replaced (if applicable) | Number of years ago that the HVAC Controls were renovated or replaced (if applicable)
refer_years_ago | Number of years ago that the Refrigeration Systems were renovated or replaced (if applicable) | Number of years ago that the Refrigeration Systems were renovated or replaced (if applicable)
window_years_ago | Number of years ago that the Windows were renovated or replaced (if applicable) | Number of years ago that the Windows were renovated or replaced (if applicable)
roof_ins_years_ago | Number of years ago that the Roof Insulation were renovated or replaced (if applicable) | Number of years ago that the Roof Insulation were renovated or replaced (if applicable)
ballast_impacted | % of the Lighting Ballasts that were renovated or replaced (if applicable) | The Percentage of the site's total Lighting Ballasts that were renovated or replaced (if applicable)
fixture_impacted | % of the Lighting Fixtures that were renovated or replaced (if applicable) | The Percentage of the site's total Lighting Fixtures that were renovated or replaced (if applicable)
control_impacted | % of the Lighting Controls that were renovated or replaced (if applicable) | The Percentage of the site's total Lighting Controls that were renovated or replaced (if applicable)
hvac_impacted | % of the HVAC Systems that were renovated or replaced (if applicable) | The Percentage of the site's total HVAC Systems that were renovated or replaced (if applicable)
hvac_control_impacted | % of the HVAC Controls that were renovated or replaced (if applicable) | The Percentage of the site's total HVAC Controls that were renovated or replaced (if applicable)
refer_impacted | % of the Refrigeration Systems that were renovated or replaced (if applicable) | The Percentage of the site's total Refrigeration Systems that were renovated or replaced (if applicable)
window_impacted | % of the Windows that were renovated or replaced (if applicable) | The Percentage of the site's total Windows that were renovated or replaced (if applicable)
roof_ins_impacted | % of the Roof Insulation that were renovated or replaced (if applicable) | The Percentage of the site's total Roof Insulation that were renovated or replaced (if applicable)
ballast_anticipate | Are you expecting to replace or renovate the Lighting Ballasts in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Lighting Ballasts
fixture_anticipate | Are you expecting to replace or renovate the Lighting Fixtures in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Lighting Fixtures
control_anticipate | Are you expecting to replace or renovate the Lighting Controls in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Lighting Controls
hvac_anticipate | Are you expecting to replace or renovate the HVAC Systems in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the HVAC Systems
hvac_control_anticipate | Are you expecting to replace or renovate the HVAC Controls in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the HVAC Controls
refer_anticipate | Are you expecting to replace or renovate the Refrigeration Equipment in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Refrigeration Equipment
window_anticipate | Are you expecting to replace or renovate the Windows in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Windows
roof_ins_anticipate | Are you expecting to replace or renovate the Roof Insulation in the next 2 years? | Yes/No/Unknown if major renovations or replacements are anticipated to take place in the next 2 years on the Roof Insulation
contact_name | Is there someone who we can contact with additional questions about building change history? | Contact Name (PC = Primary Contact)
contact_phone |  | Contact Phone Number (PC = Primary Contact)
contact_email |  | Contact Email (PC = Primary Contact)
history_comments | Additional comments: | Capture any additional context that will help inform the interview responses for the above questions. Also, capture any other changes mentioned that could impact energy use (e.g. additional floor area being added in the next 2 years)

## Mixed Use
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
mixed_use_index |  | Mixed Use Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
mixed_use_id |  | The Mixed Use ID number
mixed_use | Is this a mixed-use building / scenario? | Mixed use scenarios occur in strip malls, enclosed malls, and offices buildings with first floor retail/restaurant/grocery, situations where spaces with different businesses and different economic use types occupy the same building/complex. Each group of businesses with different economic use types must be entered as a separate Mixed-Use ID and have its own primary and detailed type. This field is always YES because buildings are only included in this table if they mixed use is applicable.
primary_econ_type | What best describes the primary economic use of the Mixed Use ID? | Indicates the primary economic use of the Mixed Use ID from the Primary Economic Use. If the building type chosen is “’12. Other,”’ describe the building. | 1.) Assembly 2.) Grocery 3.) Retail/Service 4.) Hospital 5.) Lodging 6.) Residential Care 7.) Office 8.) Restaurant 9.) School K-12 10.) University 11.) Warehouse 12.) Other 13.) Unsampled
primary_econ_type_other | If Other, Describe: | If the building type cannot be classified by the Primary Economic Use Table, describe the building.
detailed_econ_type | What best describes the detailed economic use of the Mixed Use ID? | Indicate the detailed economic use of the Mixed Used ID from the Detailed Building Type Codes Table | See DDVALS2
detailed_econ_type_other | If Other, Describe: | If the building’s detailed economic use cannot be classified from the Detailed Building Type Codes Table, describe the building.
mixed_name | Name (if different from building) | Indicate the site name if different from the building name.
area | Area (SQFT) | For each Mixed-Use ID, indicate the Mixed-Use floor area.

## General Space Information
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
space_index |  | Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
space_id |  | The Space ID number (relational to many other variables)
id1 | Mixed-Use ID (if applicable) | Indicates the appropriate Mixed-Use IDs associated with each Space ID. If Mixed-Use IDs are not assigned, the idNA will be indicated. These fields are essential for assigning the proper space id % to each mixed use area.
id2
id3
id4
idna
functional_use_code | Functional Use Code (table on page 2) | For each Space ID, indicate the functional use code of the building/complex Space ID using the Functional Use Codes (Space Type) | 1.) Assembly / Recreation 2.) Classroom 3.) Dining 4.) Guest Room 5.) Kitchen 6.) Laundry / Housekeeping 7.) Office 8.) Sales 9.) Storage – Low Bay 10.) Vacant 11.) Warehouse – High Bay 12.) Indoor Parking Garage 13.) Common Area 14.) Other
functional_use_other | If other, describe: | If functional use code is other (code 14), the space is described here
mixed_use_percent | % Of Mixed Use (if applicable) or % Total Building SQFT | For each Space ID, Indicate the Space ID’s area as a percentage of the total area associated with the Mixed-Use ID (if applicable), or the Space ID’s area as a percentage of the total building area. This number should be accurate to the nearest percent if possible. If Mixed-Use IDs are not used, the percentages for all Space IDs in a building must sum to 100. If Mixed-Use IDs are used, the percentages for all Space IDs in a Mixed-Use area must sum to 100 and the total across should add to 100% multiplied by the number of mixed use ids (if there are 3 mixed use ids, this would add to 300%)
bldg_sq_ft_percent
space_cooled | Space Cooled? | For each Space ID, indicate if the area is cooled (Y / N / Unk / Refrigerated / Frozen) | Y = Yes N = No R = Refrigerated F = Frozen NF = Not Filled UNK = Unknown
cooled_shutoff | After Hours Shutoff/Setup? | For each Space ID, indicate if the cooled area has automatic or manual after-hours shutoff/setup. | Y = Yes N = No DK = Don't Know NF = Not Filled
space_heated | Space Heated? | For each Space ID, indicate if the area is heated (Heated, Semi-Heated, Not Heated, Unknown). Semi-heated indicates a space with a heating set point below 55°F. | H = Heated SH = Semi- Heated NH = Not Heated NF = Not Filled UNK = Unknown
heated_shutoff | After Hours Shutoff/Setup? | For each Space ID, indicate if the heated area has automatic or manual after-hours shutoff/setup. | Y = Yes N = No DK = Don't Know NF = Not Filled

## Schedule
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
schedule_id |  | Schedule ID number (Primary Key)
site_id |  | The Unique Site ID
schedule_name |  | Schedule Name (numeric, created automatically upon data entry)
schedule_seq_num |  | Schedule Sequence Number
space_id1 | Space IDs Served? | Indicates the Space IDs Served by the Schedule. 1 = served 0 = not served
space_id2
space_id3
space_id4
space_id5
space_none
space_unknown
open_weeks_per_year | Weeks per year open? | For each day, indicate the weeks/year that the building/complex is open. Open can be defined as any time that tenant staff or customers occupy the building.
schedule_notes |  | Any additional notes about the schedule

## Hours
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
hour_id |  | Hours Table ID number (Primary Key)
site_id |  | The Unique Site ID
hour_sequence |  | Day of week indicator (1=Mon, 7=Sun)
schedule_id |  | Foreign key, links to Schedule table
avg_open | Avg Hours Open | For each day, indicate the number of hours that the building/complex is open for business. Public hours should be indicated for buildings with public hours versus staff hours.
avg_occupied | Avg Hours Occupied | For each day, indicate the number of hours that the building/complex is open for business plus the internal hours / maintenance (e.g., cleaning hours).
avg_hvac | Avg Hours HVAC On | For each day, indicate the number of hours that the building/complex HVAC system is scheduled to be on or in occupied mode. In facilities with HVAC that is manually turned off each night by staff this should be hours the systems is typically on or set up.
avg_lights | Avg Hours Interior Lights On | For each day, indicate the number of hours that the building/complex lights are on. If lights are controlled by OS or manual switches that track occupancy indicate “OS” or “manual” respectively.

## Energy Sources
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Energy Sources Table Index Number (Primary Key)
site_id |  | The Unique Site ID
electricity | Electricity Used on Site? (Y/N) | Indicates if Electricity is used on site | Y = Yes N = N DK = Don't Know NF = Not Filled
natural_gas | Natural Gas Used on Site? (Y/N) | Indicates if Natural Gas is used on site
oil | Oil Used on Site? (Y/N) | Indicates if Oil is used on site (indicated as 'yes' if Diesel is filled as an "other" fuel type for onsite generation)
propane | Propane Used on Site? (Y/N) | Indicates if Propane is used on site (Gas cooking or misc. equipment will be indicated if Propane is used onsite but not Natural Gas)
purchased_cooling | Purchased Cooling Used on Site? (Y/N) | Indicates if Purchased Cooling is used on site
wood | Wood Used on Site? (Y/N) | Indicates if Wood is used on site
purchased_hot_water | Purchased Hot Water Used on Site? (Y/N) | Indicates if Purchased Hot Water is used on site
purchased_steam | Purchased Steam Used on Site? (Y/N) | Indicates if Purchased Steam is used on site
other | Other Energy Sources Used on Site? (Y/N) | Indicates if other energy sources are used on site

## Electric Meter
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Electric Meter Table Index Number (Primary Key)
site_id |  | The Unique Site ID
electricmeter_id |  | Electric Meter Unique ID (assigned automatically - NOT utility meter #)
include_not_audited | Do meters include exterior & parking lighting? | Indicate whether the meters captured in the form associated with the Bill Release ID indicated above provide power to exterior and parking lighting. | Y = Yes N = N DK = Don't Know NF = Not Filled
meter_with_exterior | Do meters include consumption of areas not audited? | Indicates if Propane is used on site (Gas cooking or misc. equipment will be indicated if Propane is used onsite but not Natural Gas)

## Gas Meter
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Electric Meter Table Index Number (Primary Key)
site_id |  | The Unique Site ID
gasmeter_id |  | Gas Meter Unique ID (assigned automatically - NOT utility meter #)
include_not_audited | Do meters include exterior & parking lighting? | Indicate whether the meters captured in the form associated with the Bill Release ID indicated above provide power to areas not audited. If yes please provide notes as to the type and extent of the area covered. | Y = Yes N = N DK = Don't Know NF = Not Filled

## Generation
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Generation Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
generation_id |  | Site-specific Unique ID
generation_type | Generation Type | Indicate the type of on-site generation at the building/complex referring to the Generation Type Table: | 1.) Photovoltaics (PV) 2.) Fuel Cells (FC) 3.) Micro Turbine (MT) 4.) Large Gas Turbine (LT) 5.) Unknown (-1) 6.) Wind Turbines 7.) Reciprocating Engine (RE) 8.) None 9.) Solar Water Heat – Domestic 10.) Solar Water Heat – Pool 11.) Other
equip_operational | Is equipment operational? | Indicate whether the on-site generation equipment is functional / operational.
fuel_type | Fuel Type Code (see table) | Indicate the fuel type used by on-site generation equipment (refer to Fuel Type Table). Enter zero for none when generation uses no fuel. | 1.) Electricity 2.) Natural Gas 3.) Oil 4.) Propane 5.) Purchased Steam 6.) Purchased Hot Water 7.) Other 0.) None
fuel_type_other |  | Filled if heating fuel type is 7 - Other (Diesel is indicated as an 'other' to differentiate from fuel oil. Oil indicated on energy sources tab if diesel)
total_capacity | Total Capacity (kW) | Indicates the total peak design capacity of the on-site generation equipment (in kW). Enter -1 for unknown.
cogeneration | Is this a cogeneration system? | Indicate whether the on-site generation equipment is a cogeneration system (i.e. is some of the heat produced used to supplement space, domestic, or industrial processes?). | Y = Yes N = N DK = Don't Know NF = Not Filled
runtime | Runtime: 24/7 Peak Demand Back-up only | Indicate operational frequency of on-site generation equipment. | 247 = Runs 24/7 PD = Runs during Peak Demand BU = Back-Up only DK = Don't Know NF = Not Filled
backup_tested | If back-up only, how often is the system tested (years) | If the on-site generation equipment is used as back-up, indicate the number of years between tests. Enter 1 if tested annually and a fraction if tested more than once a year | 0.08 indicates once a month 0.02 indicates once a week
grid_connected | Is system interconnected to the grid? | Indicate if the on-site generation system is connected to the grid. | Y = Yes N = N DK = Don't Know NF = Not Filled

## Walls
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Wall Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
wall_id | NA | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Schedule.
id2
id3
id4
id5
walls_surface_type | Surface Type | This refers to the material on the EXTERIOR only. Internal composition of exterior walls is captured below in “Framing Type” and “Insulation”. Concrete block is distinguished from concrete by the presence of grout between each block. Classify Exterior Insulation and Finish Systems (EIFS) as stucco. | C = Concrete CB = Concrete Block B = Brick S = Stucco W = Wood G = Glass Curtain M = Metal V = Vinyl DK = Don't Know
walls_framing_type | Framed Wall Type | This is the framing type of the framed wall. | MS = Metal Stud MB = Metal Building W = Wood C = Concrete B = Brick DK = Don’t Know
walls_ins_material | Insulation? | Indicate the presence of any insulation irrespective of type (e.g., rigid, batt) or R-value. | Y = Yes N = N DK = Don't Know NF = Not Filled

## Windows
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Window Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
window_id | NA | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Window
id2
id3
id4
id5
window_wall_area_percent | % of Wall Area (estimate) | Estimate of the area of this window type as a percent of as a % of exterior walls. Spandrel sections are not included as windows. For instances where there are no windows present indicate 0 for the % of wall area and circle the associated Space ID’s. The remainder of this section for 0% of wall area will be blank. | Y = Yes N = N DK = Don't Know NF = Not Filled
window_opening | Window Opening | Indicates the type of window opening | 247 = Runs 24/7 PD = Runs during Peak Demand BU = Back-Up only DK = Don't Know NF = Not Filled
window_layers_of_glazing | Layers of Glazing | Number of panes of glass in the window. In the absence of plans, using a shiny object or flashlight the number of reflections indicates the number of panes.
low_e_present | Low E Present? | Indicates if there is Low-emissivity (Low E) coating present | Y = Yes N = N DK = Don't Know NF = Not Filled
cog_u_value | COG U Value | Center of Glass (COG) U-factor (BTU/SQFT*F) | This field was difficult to collect and is mostly filled with -1 for unknown
window_glazing_material | Glazing Material | Type of Glazing Material | C: Clear O: Opaque R: Reflective T: Tinted
window_frame_type | Frame Type | Type of Window Frame | M: Metal non-thermally improved. MT: Metal, thermally improved. MU: Metal, Unknown V: Vinyl W: Wood (includes metal clad wood windows)
window_covering | Blinds, shades, or other window coverings? | Indicates if there are any window coverings and if those coverings are operable or not | O: Operable Coverings F: Fixed Coverings OT: Other N: None NF: Not Filled
percent_operable | Percent Operable? (%) | Percent of total window area that can be opened. For example, if you have all residential style punched windows that slide up, the entry here would be 50%. Key here is potential not whether they are opened.

## Roofs
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Roof Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
roof_id | NA | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Roof
id2
id3
id4
id5
roof_type | Roof Type | Indicates the type of roof based on the table to the right | F: Flat. Roof slope less than 1:12 (8%). P: Pitched. Sloped roof, non-ventilated. A: Attic. Sloped roof, ventilated. R: Residential above. U: Unknown.
insulation | Insulation? | Indicate the presence of any insulation irrespective of type (e.g., rigid, batt) or R-value. | Y = Yes N = N DK = Don't Know NF = Not Filled
add_insulation | Is it possible to add additional insulation? | Is it technically and financially feasible to add insulation? E.g., for a flat built up roof, additional rigid insulation could be added the next time the roof is replaced.
roof_sf | Roof Area (SF) | This applies to flat roofs (roof type “F”) defined above. Leave blank for other roof types. Built up roofs are flat roofs (decking + rigid insulation) that are covered with sealed, waterproof. Layers.
skylights | Skylights? | Indicates if skylights installed in the roof | Y = Yes N = N DK = Don't Know NF = Not Filled
skylight_area | Skylight Area (SF) (estimate) | If skylights are installed, this indicates their cumulative area (sq. ft.)
light_dimming_control | Lighting Dimming Control? | If skylights are installed, indicates if the interior lights are dimmable and automatically controlled to maintain indoor lighting levels | Y = Yes N = N DK = Don't Know NF = Not Filled NA = NA

## Floors
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Floor Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
floor_id | NA | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Floor
id2
id3
id4
id5
floor_type | Floor Type | B: Basement. Occupied floors below grade, such as storage areas and/or mechanical spaces, having earth below. This excludes parking garages. C: Crawl space. A basement too short to stand up in, typically with a soil floor surface. S: Concrete floor slab on grade. SE: Concrete floor slab elevated above grade, such as on piers or above a parking garage. U: Unknown. N: Not Filled | B: Basement. C: Crawl space. S: Concrete floor slab on grade. SE: Concrete floor slab elevated above grade U: Unknown. N: Not Filled
floor_insulation | Insulation? | “Y” if the floor is insulated at all, such as with rigid insulation. Examples include: • Vertical insulation at slab edge and foundation. • Horizontal insulation on underside of floor slab above parking garage. | Y = Yes N = N U = Unknown NF = Not Filled

## HVAC Summary
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
hvacsummary_index |  | HVAC Summary Index Number (Primary Key)
site_id |  | The Unique Site ID
hvac_comments | Briefly describe the HVAC system (including HVAC fans, heating & cooling system) & control. | A brief description of the HVAC system and control. For common systems this should be very brief. The description should be more complete for odd systems or odd aspects of system that are not well defined by the protocol fields.

## SZ HVAC
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
szhvac_index |  | SZ HVAC Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
szhvac_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the SZ HVAC System
id2
id3
id4
id5
hvac_equip_type | Equipment Type (Table below) | Equipment type code. Enter one. See distributed single zone equipment map for examples (simple list to the right, detailed list below this table). | 1 = Rooftop Units (RTUs) 2 = Makeup Air Unit (MAU) 3 = Air Handling Unit (AHU) 4 = Furnace 5 = Heat Pump 6 = PTAC / PTHP 7 = Unit Ventilator 8 = Room AC (window unit) 9 = Unit Heater (suspended) 10 = Baseboard / Radiator 11 = Cabinet Heater (fan coil) 12 = Radiant – floor 13 = Radiant – ceiling (suspended) 14 = Swamp Cooler
heat_pump_type | If Heat Pump – Type | The heat pump type code. See distributed single zone equipment map for examples (simple list to the right, detailed list below this table). | 1 = Standard – air source 2 = Water Source – supplemental boiler and cooler 3 = Ground Source – water 4 = Ground Source – earth 5 = Ductless / Mini Split – air source 6 = VRF – single mode (either heat or cool) 7 = VRF – multimode (simultaneous heat and cool)
primary_unit_heat | Primary Unit For: | Indicates this equipment is the primary provider of Heating that supplies the selected space ID(s)
primary_unit_cool |  | Indicates this equipment is the primary provider of Cooling that supplies the selected space ID(s)
primary_unit_vent |  | Indicates this equipment is the primary provider of Ventilation that supplies the selected space ID(s)
primary_unit_none |  | Indicates this equipment provides heating, cooling and/or ventilation the selected space ID(s), but is not the primary equipment
hvac_cooling_type | Cooling Type | The mechanical cooling type of the equipment | CW = Chilled water coil. DXA = Air cooled direct expansion. DXW = Water cooled direct expansion. G = Direct ground water or water loop buried in ground E =Evaporative cooler. N = No mechanical cooling. Oth = Other cooling type NF = Not Filled DK = Don't Know
hvac_cooling_type_other |  | Filled if cooling fuel type is Other
primary_fuel_type | Primary Heat Fuel: | The primary heating fuel of the equipment. Circle one. If other, be sure to enter other fuel in the provided space. For heat pumps enter Electric. | E = Electricity NG = Natural Gas FO = Oil P = Propane OT = Other N = None NF = Not Filled
primary_fuel_type_other |  | Filled if heating fuel type is Other
primary_heating_type | Heating Type: | Indicates the heating type - Not required if electric resistance. | SE = Std. Eff. = Combustion equipment ≤ 88% efficient (output/input) CE = Condensing Eff. = Combustion equipment >88% efficient (output/input) HWC = HW-Coil = Hot Water Coil SC = Steam-Coil = Steam Coil HP = Heat Pump OT = Other DK = Don’t Know NF = Not Filled
primary_heating_type_other |  | Filled if heating type is Other
number_units | Number of Units | Number of units of this size group and type.
unit_age | Representative Age of Unit(s) (Years) | Typical age of equipment listed in this column in years (year today – year made). Integer only. Enter -1 if unknown.
unit_manuf | Representative Manufacturer | The predominant manufacturer of equipment listed in this column.
unit_model | Representative Model | The predominant model name and number of the equipment listed in this column.
unit_model_number | Representative Model Number
cooling_capacity | Rated Cooling Capacity | Average rated maximum cooling capacity of equipment listed in this column (MBtu). Enter for all equipment types. If unknown, enter -1 and 0 if no cooling. 1 MBtu = 1,000 Btu/h , 12MBtu = 1 ton
cool_capacity_range | Cooling Capacity Range (group) | The cooling capacity “bin” of the equipment listed in this column (tons). Required for all DX/HP equipment and for other cooling equipment types where the average cooling capacity is unknown. When the cooling capacity is unknown estimate this based upon air flow, unit size, and any other available information. 1 ton = 12,000Btu/h = 12MBtu
heating_capacity | Rated Heating Capacity (input) | The average maximum heating capacity of the equipment in kW or MBtu. 1Mbtu = 1 kBtu/h = 1000 Btu/h
heating_capacity_units | Specify Heating Capacity Units | The units of the rated heating capacity. | kW, MBTU, DK, NF
sup_heat_equip_type | Supplemental Heating Equipment: | Supplementary Heating Equipment type. Supplementary heating equipment should be thought as the secondary heating source in the space. For example, baseboard heaters would be selected as supplementary heating equipment when there is a primary air delivery system (e.g. RTU) also serving the same space. The supplementary heating equipment type code will generally be baseboard or fan coil. The primary HVAC unit would handle the general space heating and treatment of ventilation air while the baseboard heater handles heat loss through perimeter windows. DX and combustion equipment should never be listed as supplementary equipment. For auxiliary heat associated with heat pumps enter the same equipment type as the primary type. | Same Equipment Codes as primary_heat_type
sup_heat_fuel_type | Supplemental Heating Fuel Type: | The supplementary heating fuel type. Fuel type may or may not match primary heat source. For heat pumps this is the auxiliary heating fuel. | Same Equipment Codes as primary_heat_fuel
sup_heat_fuel_type_other |  | Filled if heating fuel type is Other
fan_control | Fan Control: | Fan control type. This can be determined from inspection of the thermostat (fan vs. auto), discussions with staff, observing whether all units are on or not, and sequence of control documentation. Variable indicates a system that has reduced flows (>30% reduction) during non-cooling hours. Typically this will be implemented as a single zone VAV system which runs at a low speed unless more air is required for cooling or to reduce CO2 levels. | C = Constant I = Intermittent V = Variable N = None Unk = Unknown NA = Not Applicable NF = Not Filled
ventilation_air | Delivery of Ventilation Air: | Do the units in this group provide outdoor air (OA) for ventilation? At unit, indicates ventilation air is brought in from outside by the unit. A unit located on the exterior wall would have an opening to introduce outside air. A unit located in the building interior would have a duct that runs to the exterior wall to receive outdoor air. Central system indicates that air from a central system (usually 100% OA system) is introduced by this system. For example, a hotel fan coil unit might receive ducted air from a central air handler to meet zone ventilation needs. Operable Window or Louver indicates outside air is introduced separately from the HVAC system. This will generally be manually activated, but in some cases can be automatically activated as part of a natural ventilation system. | AU = At Unit FCS = From Central System OW = Operable Window N = None NA = Not Applicable Unk = Unknown NF = Not Filled
economizer | Economizer: Air Water None | Do the units in this group provide economizer cooling? Water side economizer manifests in water cooled equipment when a valve directs condenser water directly to a cold water coil bypassing the DX coil or chiller. This is done when outdoor conditions are such that water temperatures leaving the heat rejection device can satisfy the cooling load without mechanical cooling. It is possible to have units with air and water economizer. | A = Air Economizer W = Water Economizer N = None DK = Don't know NA = Not Applicable NF = Not Filled
temp_control_type | Temperature Control: | Type of temperature control for the equipment. Manual–Tstat is manually operated to turn on/off the HVAC unit and set temperature set points. Many older homes have manual thermostats, but these are rarely used in commercial buildings. Programmable-Tstat has the ability to establish a variety of on/off schedules and occupied/unoccupied temperature set points. EMS-DDC describes systems that use digital controllers (e.g. computers) that are networked together and that have enhanced scheduling and programming ability. There is generally a main control terminal where the facility operator can make operational changes. Manual on/off is for units with no temperature control. | 1 = Manual T-Stat 2 = Programmable T-Stat 3 = EMS-DDC 4 = Manual On/Off DK = Don't Know NA = Not Applicable NF = Not Filled
occ_sensor_setback | Occupancy sensor used to set-up/back or turn off zone? | Are occupancy sensors used to increase the thermostat dead band, reduce supply air flow, or turn off equipment? This is often implemented at a zone level in high ventilation spaces such as classroom and conference rooms. | Y = Yes N = N DK = Don't Know NF = Not Filled NA = Not Applicable
high_vent | High Ventilation > 70% outside air | Does the system deliver a high fraction of outdoor air? Enter yes if the outdoor air fraction during heating, venting, and cooling (non-economizer) hours is over 70%. Typically systems will be 100% OA or less than 40% OA.
demand_control | Demand Controlled Ventilation? | Demand control ventilation is when the amount of outdoor air provided is controlled/varied by an in-unit or zone CO2 sensor or occupancy sensing device. Use Yes-Unk when it is determined that DCV exists but the location of the sensor is unknown. | Y-Z = Yes - In Zone Y-U = Yes - At Unit Y-Unk = Yes - Unknown N = No Unk = Unknown NA = Not Applicable NF = Not Filled
Equipment Type Codes/Description
Ducted Systems (generally)
| 1 Rooftop Units (RTUs) | Roof top package air handlers with AC and/or heating units (furnaces or heat pumps).
| 2 Makeup Air Unit (MAU) | Air handlers designed for high outside air flow fractions. Typically runs at 100% outdoor air but often has ability to run at other outside air fractions. Furnaces in makeup air units typically can modulate continuously or with fine steps to very low part loads.
| 3 Air Handling Unit (AHU) | Air handler with hydronic or split system (AC/HP) heating and/or cooling.
| 4 Furnace | Package air handler with combustion heating. Can also have split system AC. Electric furnace should be recorded as system type 3 – AHU.
| 5 Heat Pump | Air hander with heat pump heating. Includes package and split heat pumps except those included in 1.
Non Ducted Systems (generally)
| 6 PTAC / PTHP | Package terminal AC and HP units. Permanently installed. Typical in hotel/motel.
| 7 Unit Ventilator | Unducted fan coil unit that provides outdoor air and has hydronic or electric heating and/or cooling.
| 8 Room AC | Room AC, typically window units but also including portable spot cooling solutions.
(window unit)
| 9 Unit Heater (suspended) | Unducted fan coil unit providing hydronic, electric or furnace heating and/or hydronic cooling but no ventilation.
| 10 Baseboard / Radiator | Hydronic and electric baseboards and hydronic radiators.
| 11 Cabinet Heater | Fan coil unit that provides hydronic or electric heating and/or cooling. This covers any fan coil unit that’s not explicitly addressed by other equipment type codes.
(fan coil)
| 12 Radiant – floor | Hydronic or electric radiant floor heat.
| 13 Radiant – ceiling (suspended) | All forms of radiant heat except for radiant floors.
| 14 Swamp Cooler | An evaporative cooler. Generally 100% outdoor air units that only run to provide cooling.
Heat Pump Type Codes
| 1 Standard – air source | Package or split air source heat pumps except for ductless split systems defined in 5-8.
| 2 Water Source | Water source heat pumps connected to common water loop with supplemental boiler and cooling tower.
| 3 Ground Source – water | Water source heat pumps connected to common water loop and uses heat exchanger with ground water loop on other side. May have supplemental boiler.
| 4 Ground Source – earth | Water source heat pumps connected to common water loop where water loop is buried in ground through large piping system. May have supplemental boiler.
| 5 Ductless / Mini Split | Air source variable speed split HP with refrigerant system serving 2 or less terminals. Typically less than 2.5 tons and unducted.
| 6 VRF –Single mode | Air or water source variable speed split HP with refrigerant system serving multiple terminals. No simultaneous heat/cool, all terminals are in the same mode. Water source may have supplemental boiler and cooling tower.
| 7 VRF –multimode | Air or water source variable speed split HP with refrigerant system serving multiple terminals. Simultaneous heat/cool at different terminals on same system. 3-pipe systems are most common, but 2 pipe systems are possible. Water source may have supplemental boiler and cooling tower.

## MZ HVAC
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
mzhvac_index |  | MZ HVAC Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the SZ HVAC System
id2
id3
id4
id5
mzhvac_id |  | Site-specific Unique ID
fan_system_type | Fan System Type (Table below) | Fan System type code. Enter one. (simple list to the right, detailed list below this table). | 1 = Single Zone 2 = Dual Duct 3 = Single Duct - Reheat 4 = Multizone 5 = VVT 6 = DOAS 7 = Makeup Air Unit (MAU) 8 = Other
fan_system_type_other |  | Filled if Fan system type is Other
primary_unit_heat | Primary Unit For: | Indicates this equipment is the primary provider of Heating that supplies the selected space ID(s)
primary_unit_cool |  | Indicates this equipment is the primary provider of Cooling that supplies the selected space ID(s)
primary_unit_vent |  | Indicates this equipment is the primary provider of Ventilation that supplies the selected space ID(s)
primary_unit_none |  | Indicates this equipment provides heating, cooling and/or ventilation the selected space ID(s), but is not the primary equipment
airflow_control | Airflow Control: | The supply fan control. Constant Volume (CV) operation is where the primary air volume does not significantly change in response to zone loads. Variable Air Volume (VAV) control requires primary air turndown of at least 50% in response to zone loads. Stepped Constant Volume (SCV) requires essentially constant volume operation but with time of day reduction in flows. | CV = Constant Volume SCV = Stepped Constant Vol. VAV = Variable Air Volume DK = Don't Know NF = Not Filled
hvac_cooling_type | Cooling Type: | The mechanical cooling type of the equipment. Circle one. | CW = Chilled water coil. DXA = Air cooled direct expansion. DXW = Water cooled direct expansion. GC = Direct ground water or water loop buried in ground E =Evaporative cooler. N = No mechanical cooling. Oth = Other cooling type NF = Not Filled DK = Don't Know
primary_fuel_type | Primary Heating Fuel: | The primary heating fuel of the equipment. Circle one. Enter Electric for heat pumps. | E = Electricity NG = Natural Gas FO = Fuel Oil P = Propane OT = Other N = None NF = Not Filled
primary_fuel_type_other |  | Filled if heating fuel type is Other
primary_heating_type | Heating Type: | The heating type. | SE = Std. Eff. = Combustion equipment ≤ 88% efficient (output/input) CE = Condensing Eff. = Combustion equipment >88% efficient (output/input) HWC = HW-Coil = Hot Water Coil SC = Steam-Coil = Steam Coil HP = Heat Pump OT = Other DK = Don’t Know NF = Not Filled
primary_heating_type_other |  | Filled if cooling fuel type is 7 - Other
heat_pump_type | If Heat Pump – Type | The heat pump type code. See distributed single zone equipment map for examples (simple list to the right, detailed list below this table). | 1 = Standard – air source 2 = Water Source – supplemental boiler and cooler 3 = Ground Source – water 4 = Ground Source – earth 5 = Ductless / Mini Split – air source 6 = VRF – single mode (either heat or cool) 7 = VRF – multimode (simultaneous heat and cool)
terminal_reheat_energy | Terminal Reheat Energy: | Terminal reheat energy type. Reheat is limited to systems that deliver cold air that must then be reheated in some zones. Enter None if no reheat present. | E = Electric W = Hot Water S = Steam N = None OT = Other DK = Don't Know NF = Not Filled
number_units | Number of Units | Number of units of this size and type.
airflow_capacity | Airflow Capacity (CFM) | The average primary supply air flow this group. Enter -1 if unknown
unit_age | Representative Equipment Age (Years) | Typical age of equipment listed in this column in years (year today – year made). Exact, or estimate whichever is available. Integer only. Enter -1 if unknown.
unit_manuf | Representative Manufacturer | The predominant manufacturer of equipment listed in this group. -1 if unknown
unit_model | Representative Model Name/Number | The predominant model name and number of the equipment in this column. -1 if unknown
unit_model_number
cooling_capacity | Rated Cooling Capacity | Average rated maximum cooling capacity of equipment listed in this column (MBtu). Enter for all equipment types. If unknown, enter -1 and 0 if no cooling. 1 MBtu = 1,000 Btu/h , 12MBtu = 1 ton
cool_capacity_range | Cooling Capacity Range (tons) | The cooling capacity “bin” of the equipment listed in this column (tons). Required for all DX/HP equipment and for other cooling equipment types where the average cooling capacity is unknown. When the cooling capacity is unknown estimate this based upon air flow, unit size, and any other available information. 1 ton = 12,000Btu/h = 12MBtu
heating_capacity | Rated Heating Capacity (input) | The average maximum heating capacity of the equipment in kW or MBtu. 1Mbtu = 1 kBtu/h = 1000 Btu/h
heating_capacity_units | Specify Heating Capacity Units | The units of the rated heating capacity. | kW, MBTU, DK, NF
air_distrib_system | Air Distribution System: | Air distribution type. Circle One. Overhead = ductwork run to air diffusers located overhead, typically in a suspended ceiling. Underfloor = open air plenum underfloor with manual or automatic floor diffusers. Low Wall = ductwork run to air diffusers located low on a wall or in floor. Also referred to as displacement system. Other: __________ | Ov = Overhead U = Underfloor W = Low Wall OT = Other DK = Don’t Know NF = Not Filled
air_distrib_system_other |  | Filled if Air Distribution Type = Other
supply_fan_vol_control | Supply Fans: Volume Control: | Means of controlling fan delivered airflow: None = no device used. Inlet Vane = set of louvers on inlet of fan. Discharge damper = set of dampers on fan discharge. VFD = variable frequency drive that controls fan rotational speed. Bypass Damper = set of dampers and ducting on fan discharge that return a percentage of airflow to inlet side of fan. | N = None IV = Inlet Vane D = Discharge Damper V = VFD B = Bypass Damper UNK = Unknown NF = Not Filled
supply_motor_hp | Supply Fans Motor HP | Total HP of supply motors. Should be system total, not per unit. Enter -1 if unknown.
return_or_exhaust_fan | Return Fans and /or Exhaust Fans? | Do the units in this group have return and/or exhaust fans. | Y = Yes N = N DK = Don't Know NF = Not Filled
motor_hp | Motor HP | Total HP of return and exhaust motors. Should be system total, not per unit. Enter -1 if unknown.
terminal_standard | VAV Terminal Type: | VAV terminal type. Required in all systems with VAV terminals. Indicates all that apply with a 1. Standard Induction = Standard fanless units Induction = Fanless units that induce plenum air into the air stream as it is introduced to the zone. FPB-Parallel = Fan powered parallel units FPB-Series = Fan powered series units None = no device used. Typically systems with fan powered terminals will also have standard terminals. The fan in FPS units runs continuously, the fans in FPP units only run when heating is required. Induction terminals should be rare.
terminal_induction
terminal_fpb_parallel
terminal_fpb_series
terminal_none
terminal_unknown
temp_control_type | Temperature Control: | Type of temperature control for the equipment. Manual–Tstat is manually operated to turn on/off the HVAC unit and set temperature setpoints. Many older homes have manual thermostats, but are rarely used in commercial buildings. Programmable-Tstat has the ability to establish a variety of on/off schedules and occupied/unoccupied temperature setpoints. EMS-DDC describes systems that use digital controllers (e.g. computers) that are networked together and that have enhanced scheduling and programming ability. There is generally a main control terminal where the facility operator can make operational changes. Manual on/off is for units with no temperature control. | 1 = Manual T-Stat 2 = Programmable T-Stat 3 = EMS-DDC 4 = Manual On/Off DK = Don't Know NA = Not Applicable NF = Not Filled
demand_control | Demand Controlled Ventilation Type: | Demand control ventilation is when the amount of outdoor air provided is controlled/varied by an in-unit or zone CO2 sensor or occupancy sensing device. Use Yes-Unk when it is determined that DCV exists but the location of the sensor is unknown. | Y-Z = Yes - In Zone Y-U = Yes - At Unit Y-Unk = Yes - Unknown N = No Unk = Unknown NA = Not Applicable NF = Not Filled
occ_sensor_setback | Occupancy sensor used to set-up/back or turn off zone? | Are occupancy sensors used to increase the thermostat dead band, reduce supply air flow, or turn off equipment? This is often implemented at a zone level in high ventilation spaces such as classroom and conference rooms. | Y = Yes N = N DK = Don't Know NF = Not Filled
high_vent | High Ventilation > 70% outside air | Does the system deliver a high fraction of outdoor air? Enter yes if the outdoor air fraction during heating, venting, and cooling (non-economizer) hours is over 70%. Typically systems will be 100% OA or less than 40% OA. | Y = Yes N = N DK = Don't Know NF = Not Filled
economizer | Economizer? | Do the units in this group provide economizer cooling? Water side economizer manifests in water cooled equipment when a valve directs condenser water directly to a cold water coil bypassing the DX coil or chiller. This is done when outdoor conditions are such that water temperatures leaving the heat rejection device can satisfy the cooling load without mechanical cooling. Units that provide outdoor air cooling when needed but do not have mechanical cooling are considered to have economizer. | A = Air Economizer W = Water Economizer N = None DK = Don't know NA = Not Applicable NF = Not Filled
exhaust_heat_recovery | Exhaust Air Heat Recovery? | Presence of exhaust air heat recovery. Heat may be used to preheat incoming outdoor air or for another purpose. Exhausting building air to the garage is not considered heat recovery. | Y = Yes N = N DK = Don't Know NF = Not Filled
heat_recovery_type | Heat Recovery Type | Type of heat recovery. Circle one. | E = Exhaust Air R = Refrigeration C = Condenser DK = Don't Know NF = Not Filled
Fan System Type Codes
1 Single Zone | Single zone air systems. Limited to specialty systems. NOTE: reheat terminals and duct heaters do not need to be entered as separate entries from the main AHU. Common configurations are defined below: Single Zone, Constant Volume – Air is supplied to a space or spaces at constant rate. Air handling unit includes a cooling coil and/or heating coil that varies the temperature of the air leaving the main unit based upon zone temperature. Generally controlled by a single thermostat but occasionally two or more thermostats will be averaged into a single control signal. Air can be delivered to multiple spaces but the temperature of the air will not vary by space and the fraction of total supply air supplied to each space will be constant.. Single Zone, Constant Volume, Terminal Reheat – Typically used for specialty applications where humidity control is important (ex: hospital operating rooms). Cooling coil to cool and dehumidify air along with reheat coil for temperature control. High energy usage – Since the cooling coil is controlled to maintain the humidity level, the air may be overcooled and thus reheating is required to compensate for overcooling. Single Zone, Variable Air Volume – Single zone VAV systems use a cooling coil to produce chilled air at a constant temperature. Airflow is increased or decreased in response to the space thermostat by adjusting dampers or the speed of the fan (Variable Control). Unit may also be equipped with an additional coil for heating. Single Zone, Variable Air Volume, Terminal Reheat – Same as Single Zone, Variable Air Volume but with the addition of reheat terminals. Reheat coil for temperature control. Often used for perimeter heating in combination with simple VAV terminals for the interior.
2 Dual Duct | Separate Hot Air and Cold Air Supply ducts which run throughout the building to each terminal unit. Hot and Cold air is then mixed at a mixing box at each zone location. Mixing boxes are controlled with dampers to vary the quantity of warm and chilled air in response to the zone thermostat. Constant Volume or Variable Air Volume operation. Systems can have a single supply fan and split the air streams or can have separate supply fans. Common configurations are defined below: Dual Duct, Constant Volume – Separate ducts for hot and cold airstreams which are mixed in dual duct boxes for each zone. Typically a single fan air handler. Dual Duct, Variable Air Volume – Single or multiple supply fans typically controlled via static pressure sensors. Enhanced energy efficiency
3 Single Duct - Reheat | Single duct air system delivering cool air to multiple zones. The cooling coil or economizer chills air to the same temperature for all zones. Terminal equipment at each zone has dampers to reduce the flow of cool air and/or steam, hot water, or electric reheat coils controlled by the zone thermostat. Common configurations are defined below: Single Duct, Constant Volume, Terminal Reheat – Reheat system allows zone control by reheating the cool airflow to the temperature required for the particular zone. This is an older system type though can still found in newer medical settings. Single Duct, Variable Air Volume – Variable air volume control damper controlled by zone thermostat in each zone. Damper acts as a throttle to allow more or less cool air into the zone. Single Duct, Variable Air Volume, Terminal Reheat – Addition of reheat coil to Single Duct VAV system. Allows for heating of air in addition to volume control.
4 Multizone | Air handler producing warm and cold air that is mixed at the air handler to deliver air at a temperature customized for each zone. A single duct conducts air from the air handler mixing box to the zone. This is generally older system style. MZ system means that hot air and cold air are mixed for each zone AT THE AIR HANDLER, and then a dedicated duct conveys the air to each zone. In general, there should be no reheat and no VAV terminals. Separate duct to each zone. This is a specific and uncommon system type. It DOES NOT include single zone units that deliver air to multiple separate spaces at a single temperature and volume fraction. It DOES NOT include unknown systems that serve multiple zones.
5 VVT | Constant volume air hander that delivers variable air flow to the zones utilizing a bypass damper. Generally the system will deliver heating or cooling not both. This is generally older system style. Variable Volume and Temperature – Air volume delivered to the zones is controlled by zone dampers. Main fan typically has no volume control and system pressure simply increases as zone dampers close or there is a bypass damper to shunt air from the supply ducts directly to the return duct.
6 DOAS | System delivering ventilation air to zones with limited heating and cooling. Heating and cooling are primarily provided by other systems such as chilled beams and perimeter radiation which do not provide ventilation air except possibly as economizer cooling. Often combined with exhaust air system and heat exchanger.
7 Makeup Air Unit (MAU) | Larger air handler that in typical operating modes conditions 100% outside air and has no recirculated air. Units can have capabilities to recirculate air.
8 Other | If the fan system type is not represented above, describe the fan system type in detail in the description with reference to the column being described.
Heat Pump Type Codes
1 Standard – air source | Package or split air source heat pumps except for ductless split systems defined in 5-8.
2 Water Source | Water source heat pumps connected to common water loop with supplemental boiler and cooling tower.
3 Ground Source – water | Water source heat pumps connected to common water loop and uses heat exchanger with ground water loop on other side. May have supplemental boiler.
4 Ground Source – earth | Water source heat pumps connected to common water loop where water loop is buried in ground through large piping system. May have supplemental boiler.
5 Ductless / Mini Split | Air source variable speed split HP with refrigerant system serving 2 or less terminals. Typically less than 2.5 tons and unducted.
6 VRF –Single mode | Air or water source variable speed split HP with refrigerant system serving multiple terminals. No simultaneous heat/cool, all terminals are in the same mode. Water source may have supplemental boiler and cooling tower.
7 VRF –multimode | Air or water source variable speed split HP with refrigerant system serving multiple terminals. Simultaneous heat/cool at different terminals on same system. 3-pipe systems are most common, but 2 pipe systems are possible. Water source may have supplemental boiler and cooling tower.

## Boilers
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
boiler_index |  | MZ HVAC Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
boiler_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the SZ HVAC System
id2
id3
id4
id5
boiler_service | Boiler Service: | Boiler service type or working fluid. Either Steam or Hot Water | Steam Hot Water -1 = Unknown
fuel_type | Fuel Type | The fuel code for the primary fuel used by the boiler. | 1.) Electricity 2.) Natural Gas 3.) Oil 4.) Propane 5.) Purchased Steam 6.) Purchased Hot Water 7.) Other 0.) None -1.) Unknown
back_up_fuel_type | Backup Fuel Type | The fuel code of any boiler back up fuel.
number_identical_boilers | Number of Identical Boilers | The number of boilers covered by this entry. Includes redundant units.
number__standby_units | Number of Redundant Units | Number of boilers in this entry that are used strictly for backup.
age_of_boiler | Age of Boiler(s) (years) | Typical age of equipment listed in this column in years (year today – year made). Enter -1 if unknown.
manufacturer | Boiler Manufacturer | The boiler manufacturers name.
model_name_number | Model Name/Number | The boiler model name and number.
input_capacity_mbtu_total | Input Capacity (MBTU Total) | Total input capacity of boiler burners in this group (MBTU) Enter -1 in unknown.
heat_recovery | Heat Recovery | Is heat recovered from the boiler flue gas (sometimes called a “stack economizer”) or from steam boiler blow down water? | Y = Yes N = N -1 = Unknown NF = Not Filled
heat_recovery_type | Heat Recovery Type | Indicates type of heat recovery. Flue gas heat recovery is also known as a “stack economizer”. Blow-down indicates heat recovery from steam boiler blow down systems. | FG = Flue Gas BD = Blow Down OT = Other -1 = Unknown N = None NA = NA NF = Not Filled
heat_recovery_other | Heat Recovery Type- Other | If heat recovery type is other, this field is filled
condensing | Condensing? | Is the boiler a condensing boiler? Efficiency ( rated or input/output ) > 88%. | Y = Yes N = N -1 = Unknown NF = Not Filled
boiler_function | Boiler Functions Served: Space Heat DHW Process Combo | Indicate all of the loads the boiler serves. Space Heat only, DHW only, Process only, or a combination. Combo entered for boilers with more than one function. Pool and Spa boilers are included as Process | SH = Space Heat Only DHW = DHW only P = Process only C = Combination
primary_quantity | Primary Distribution Pump Quantity | Number of pumps associated the primary heating loop through the boilers in this column. The pump columns correspond to the boiler. If a common pump is used by more than one boiler entry, enter it in one column only. If pumps have different capacity control, enter the control of the lead pump. Include active and redundant pumps.
primary_num_standby_units | Number of Redundant Units | Number of pumps in this column used strictly for backup
primary_motor_hp | Motor HP (Total) | Total motor nameplate HP. If name plate not available enter brake HP if available otherwise enter -1. Total for boiler system and all pumps together, not per pump.
primary_capacity_control | Capacity Control: | How is the pump capacity controlled? 1 and 2 speed motors are constant speed motors operating continuously or cycling. The 2- speed motor also changes speed as needed. Variable is for pumps with VFD motor drive. | 1 = 1 Speed 2 = 2 Speed V = Variable -1 = Unknown NF = Not Filled
primary_ems_control | EMS Control? | Are the pumps controlled by or hooked up to the EMS system? Enter Y if the pumps have a DDC connection that could control the pumps even if the pumps run continuously. | Y = Yes N = N -1 = Unknown NF = Not Filled
secondary_quantity | Secondary (or Space Heat) Distribution Pump Quantity | Number of pumps associated the secondary heating loop through the boilers in this column.
secondary_num_standby_units | Number of Secondary Redundant Units | Number of pumps in this column used strictly for backup
secondary_motor_hp | Motor HP (Total) | Total motor nameplate HP. If name plate not available enter brake HP if available otherwise enter -1. Not per pump but total for boiler system.
secondary_capacity_control | Capacity Control: | How is the pump capacity controlled? 1 and 2 speed motors are constant speed motors operating continuously or cycling. The 2- speed motor also changes speed as needed. Variable is for pumps with VFD motor drive. | 1 = 1 Speed 2 = 2 Speed V = Variable -1 = Unknown NF = Not Filled
secondary_ems_control | EMS Control? | Are the pumps controlled by or hooked up to the EMS system? Enter Y if the pumps have a DDC connection that could control the pumps even if the pumps run continuously. | Y = Yes N = N -1 = Unknown NF = Not Filled

## Chiller
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
chiller_index |  | MZ HVAC Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
chiller_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the SZ HVAC System
id2
id3
id4
id5
compressor_type | Compressor Type | Compressor type code from compressor code list. If chilled water is provided by an unaudited plant then enter the type code for “off-site”. Chiller compressor types can be difficult to identify. Model numbers and product literature are the best source of information. (simple table to the right, detailed table below) | 1 = Centrifugal 2 = Reciprocating 3 = Screw 4 = Scroll 5 = Absorption, Nat Gas 6 = Absorption, Steam 7 = Other -1 = Unknown NF = Not Filled
num_identical_chillers | Number of Identical Chillers | The number of chillers covered by this entry. Include redundant chillers.
num_standby_units | Number of Redundant Units | Number of chillers in this entry that are used strictly for backup. Ask how many are chillers backup, or how many are used regularly during summer hot spells (the unused units would be entered here).
chiller_age | Age of Chiller(s) (Years) | Age of the chiller in years (integer only). Exact, or nearest 5-10 years whichever is available. Enter -1 if unknown.
chiller_manufacturer | Manufacturer | The chiller manufacturers name.
chiller_model_name_num | Model Name/Number | The chiller model name and number.
rated_cooling_capacity | Rated Cooling Capacity | The average chiller output capacity. Enter -1 in unknown. 1 ton = 12,000Btu/h = 3.515kW.
rated_capacity_units | Rated Capacity Units | The units of the rated cooling capacity, kW or tons. Generally this will be tons. | Tons, KW, DK or NF (not filled)
water_side_economizer | Water side economizer? | A chiller with a waterside economizer has valves that during cold weather let water bypass the chiller and go to the cooling tower directly. | Y = Yes N = N DK = Don't Know NF = Not Filled
compressor_vfd | Compressor VFD? | Centrifugal, screw, and scroll compressors can have VFD drives. This is usually integral to the unit so the drive may be difficult to locate. | Y = Yes N = N DK = Don't Know NF = Not Filled NA = NA
hr_condenser_type | Heat Rejection Condenser Type | Enter the condenser type code for the heat rejection equipment serving the chiller group listed in the same column. An entry must also be made for heat rejection equipment serving water cooled DX equipment. This should be in a column with no chiller entered above. Add additional pages as required. Do not enter heat rejection equipment twice. If heat rejection equipment serves multiple chiller entries, enter it in one column only. If “other” provide description. (simple table to the right, detailed table below) | 1 = Air Cooled Refrigerant 2 = Evaporative Cooler Refrigerant 3 = Water Cooled Fluid 4 = Air Cooled Fluid 5 = Other -1 = Unknown NF = Not Filled
hr_fan_control | HR Fan Control: | Type of condenser fan control. VFD control will often be visible. | CO = Constant On CY = Constant Cycle TM = Two motors TS = Two-Speed motor V = Variable Speed Unk = Unknown NF = Not Filled
hr_num_identical_condensers | Number of Identical HR Condensers | Number of identical condensers. Enter zero if there are no condensers for the associated chiller (compressor type = off-site). Include redundant units in this count.
hr_num_units_standby | Number of Redundant Units | Number of condensers used strictly for backup. Ask whether all units are used or whether some are used only for back up. Get count.
hr_motor_hp | Fan Motor HP (Total) | Total fan motor HP for all fans in the condenser. If the auditor treats a multi-cell condenser as some number of identical condensers then this would be the motor HP for single cell. If a condensing unit with a number of cells is treated as one unit then the total HP of all motors in the unit would be entered. If there is small pony motor that runs only when the large motor isn’t on, then only include the larger motor.
hr_ems_control | EMS Control? | Are the fans controlled by or hooked up to the EMS system? Enter Y if the condenser or tower has a DDC connection that does or could control the units.
condenser_heat_recovery | Condenser Heat Recovery | Presence of condenser heat recovery to recover heat for some use, typically hot water or outdoor air-preheat.
primary_num_identical_pumps | Primary Distribution Pump Quantity | Number of pumps associated the primary cooling loop through the chillers. The columns are meant to correspond to the chiller columns above. Enter pumps below the chiller they serve, but only enter the pumps in one column. If a common pump is used by more than one chiller entry, enter it one column only. Count is inclusive of redundant units.
primary_num_standby_units | Number of Redundant Units | Number of pumps used strictly for backup. Ask whether all pumps are used or whether some are used only for back up. Get count.
primary_motor_hp | Motor HP (Total) | Total motor nameplate HP. If name plate not available enter brake HP if available otherwise enter -1.
secondary_num_identical_pumps | Cooling Water Distribution Pumps (Secondary) Number of Identical Pumps | Number of pumps associated a secondary cooling loop that circulate water to the building and do not circulate water through the chiller. The pump columns are meant to correspond to the chiller columns above. Enter pumps below the chiller entry they serve, but only enter pumps once. If a common pump is used by more than one chiller entry, enter it one column only. Enter zero if there are no secondary pumps. Count is inclusive of redundant units.
secondary_num_standby_units | Number of Secondary Redundant Units | Number of pumps used strictly for backup. Ask whether all pumps are used or whether some are used only for back up. Get count.
secondary_motor_hp | Motor HP (Total) | Total motor nameplate HP. If name plate not available enter brake HP if available otherwise enter -1.
secondary_capacity_control | Capacity Control: | How is the pump capacity controlled? 1 and 2 speed motors are constant speed motors operating continuously or cycling. The 2-speed motor also changes speed as needed. Variable is for pumps with VFD motor drive. | 1 = 1 Speed 2 = 2 Speed V = Variable -1 = Unknown NF = Not Filled
secondary_ems_control | EMS Control? | Are the pumps controlled by or hooked up to the EMS system? Enter Y if the pumps have a DDC connection that could control the pumps even if the pumps run continuously. | Y = Yes N = N -1 = Unknown NF = Not Filled
wp_num_identical_pumps | Heat Rejection Water Pumps Number of Identical Units | Number of pumps associated the condenser water loop between the chillers or DX equipment and the cooling tower or dry cooler. The pump columns are meant to correspond to the condenser columns above. Enter pumps below the condenser entry they serve but only enter the pumps in one column. If a common pump is used by more than one chiller entry, enter it one column only. An entry must also be made for heat rejection equipment serving water cooled DX equipment. This should be entered in a column with no chiller entered above. Add additional pages as required. Enter zero if there are no secondary pumps. Count is inclusive of redundant units.
wp_num_standby_units | Number of Secondary Redundant Units | Number of pumps used strictly for backup. Ask whether all pumps are used or whether some are used only for back up. Get count.
wp_motor_hp | Motor HP (Total) | Total motor nameplate HP. If name plate not available enter brake HP if available otherwise enter -1.
wp_capacity_control | Capacity Control: | How is the pump capacity controlled? 1 and 2 speed motors are constant speed motors operating continuously or cycling. The 2-speed motor also changes speed as needed. Variable is for pumps with VFD motor drive. | 1 = 1 Speed 2 = 2 Speed V = Variable -1 = Unknown NF = Not Filled
wp_ems_control | EMS Control? | Are the pumps controlled by or hooked up to the EMS system? Enter Y if the pumps have a DDC connection that could control the pumps even if the pumps run continuously. | Y = Yes N = N -1 = Unknown NF = Not Filled
Compressor Type Codes
| 1 Centrifugal | Rotating wheel located within discharge housing, much like an AHU fan. Determine from nameplate, make and model, or O&M materials.
| 2 Reciprocating | Piston moving up and down within a cylinder, much like car engine. Determine from nameplate, make and model, or O&M materials.
| 3 Screw | Two counter – rotating shafts, much like a meat grinder. Determine from nameplate, make and model, or O&M materials. Screws are two counter-rotating shaft
| 4 Scroll | Scroll or spirals rotating one into the other. Determine from nameplate, make and model, or O&M materials.
| 5 Absorption, natural gas | Uses two different fluids (H2O/ammonia) with different adsorption/dissolving and evaporation/condensing properties. Absorption chiller with gas fired combustion burner included as part of unit.
| 6 Absorption, steam | Uses two different fluids (H2O/ammonia) with different adsorption/dissolving and evaporation/condensing properties. Absorption chiller utilizing steam from separate boiler or steam generator.
| 7 Off-site | This type indicates chilled water is delivered to the audited area from a source outside of the audit scope. This typically would be from a district chilled water system or central plant that is not within the audit scope
Heat Rejection Condensing Type Codes
| 1 Air cooled refrigerant | Air cooled refrigerant condensers are common in package air cooled chillers. Typically refrigerant copper tubing with aluminum fins to enhance heat transfer.
| 2 Evaporative cooled refrigerant | Refrigerant is cooled by unit with external water spray to produce evaporative effect on the refrigerant coils.
| 3 Water cooled fluid | Cooling tower with wetted media that uses evaporative cooling effect. Cooled water is pumped to condenser heat exchanger(s).
| 4 Air cooled fluid | Cooling tower with dry fin and tube heat exchanger that uses sensible cooling. Cooled water is pumped to condenser heat exchanger(s). Sometimes referred to as a dry cooler
| 5 Other | Provide description of any equipment coded as other.

## Building Controls
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
controls_id |  | Automation Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
seq_num |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Automation Controls
id2
id3
id4
id5
full_dcc | Full DDC (major equipment & zone level) (FD) | Full DDC control has central DDC control of major equipment and communicating DDC control of zone equipment and thermostats. | FD = Yes - Full DDC Unk = Unknown NF = Not Applicable
hybrid_pneumatic | Hybrid – Pneumatic (DDC at major Equip & Pneumatic at zone level (HP) | Hybrid-Pneumatic control has central DDC control of major equipment and pneumatic control of zone equipment and thermostats (thermostats are not electronic). Pneumatic controls use compressed air to transfer control signals. This is primarily located in older buildings where DDC has been retrofitted. Pneumatic control is a control method that uses compressed air. The thermostats are not electronic. | HP = Yes - Hybrid-Pneumatic Unk = Unknown NF = Not Applicable
hybrid_electric | Hybrid -Electric (DDC at major Equip & electronic at zone level) (HE) | Hybrid-Electric has central DDC control of major equipment and non-communicating electronic control of zone equipment and thermostat. | HE = Yes - Hybrid Electric Unk = Unknown NF = Not Applicable
full_pneumatic | Full Pneumatic (FP) | Full Pneumatic means all system controls, major equipment, zone level equipment, and zone thermostats are pneumatic with no electronic controls. Pneumatic controls use compressed air as the means of generating and transmitting the control signals. | FP = Yes - Full Pneumatic Unk = Unknown NF = Not Applicable
full_electronic_manual | Full Electronic – Manual T-stat | Full Electronic means all controls for major equipment, zone equipment, and thermostats are electronic controls (e.g. typical programmable thermostat) that do not report to a central DDC system. FEM refers to Manual Thermostats and FEP refers to programmable thermostats. Circle either Programmable or Manual | FEM = Yes - Full Electronic (Manual T-Stat) FEP = Yes - Full Electronic (Programmable T-Stat) Unk = Unknown NF = Not Applicable
full_electronic_programmable | Full Electronic – Programmable T-stat
config_other | Other (e.g. at unit only) | Describe any “Other” controls in the right margin. Prime example is a unit that you control by manually turning it on and off. | OT = Yes - Other Controls Unk = Unknown NF = Not Applicable
config_other_entry |  | If other is identified, this field will be filled | FD = Yes - Full DDC Unk = Unknown NF = Not Applicable
time_clock_start | Time clock start / stop function (T) | Is the HVAC system controlled by a time clock which turns the system off and on based on time of day? | T = Yes - Timeclock Unk = Unknown NF = Not Applicable
optimum_start | Optimum start / stop (O) | Optimum start control adjusts the HVAC start time based upon outdoor or space conditions so HVAC warm-up/cool-down operation time is minimized. In some thermostats, this is referred to as adaptive recovery. | O = Yes - Optimum Unk = Unknown NF = Not Applicable
unocc_temp_setback | Unoccupied temperature setback (UB) | Is there an unoccupied period where space heating temperature set point is reduced either electronically or by regular staff operation? Set back must be at least 5F to qualify. | UB = Yes - Setback Unk = Unknown NF = Not Applicable
unocc_temp_setup | Unoccupied temperature setup (UU) | Is there an unoccupied period where space cooling temperature set point is increased either electronically or by regular staff operation? Set up must be at least 5F to qualify. | UU = Yes - Setup Unk = Unknown NF = Not Applicable
air_handler_na | Does the building have MZ systems that the following Questions would apply to? | Yes or no. If no, then the next 3 variables will all be NF | Y = Yes N= No DK = Don't know NF = Not filled
supply_temp_reset | Supply air temperature reset (S) | In reheat or mixing systems, is the central supply air temperature automatically adjusted based upon zone temperature, zone terminal damper position, outdoor air temperature, or other means. | S = Yes - Supply Temp Reset Unk = Unknown NF = Not Applicable
static_pressure_reset | Static pressure reset (P) | In VAV systems, is the central supply air pressure set point adjusted based upon something (zone temperature, zone terminal damper position, outdoor air temperature, season, or other). | S = Yes - Static Pressure Reset Unk = Unknown NF = Not Applicable
zone_damper_air_reset | Zone damper airflow reset (Z) | In systems with VAV terminals, are the zone terminal minimum airflows lowered (e.g. 30 – 50%) prior to terminal reheat is turned on. | S = Yes - Zone Damper Reset Unk = Unknown NF = Not Applicable
hydronic_na | Does the building have Hydronic Loops that the following questions would apply to? | Yes or no. If no, then the next 3 variables will all be NF | Y = Yes N= No DK = Don't know NF = Not filled
hot_water_temp_reset | Hot water temperature reset (HW) | Hot water temperature reset is when the hot water circulation loop temperature is automatically reduced when ambient conditions are warmer or heating loads are low. Controller is sometimes visible on boiler. | HW = Yes - Hot Water Reset Unk = Unknown NF = Not Applicable
chilled_water_temp_reset | Chilled water temperature reset (CHW) | Chilled water temperature reset is when the chilled water circulation loop temperature is automatically increased when ambient conditions are colder or cooling loads are low. | CHW = Yes - Chilled Water Reset Unk = Unknown NF = Not Applicable
cond_water_temp_reset | Condenser water temperature reset (CW) | Condenser water temperature reset is when the condenser water circulation loop temperature is automatically decreased when ambient conditions are colder or cooling loads are low. | CW = Yes - Condenser Water Reset Unk = Unknown NF = Not Applicable
noted_control_troubles | Noted Control Troubles | Any control troubles noted by the site staff. | Y = Yes N= No DK = Don't know NF = Not filled
vent_ao | Garage Exhaust Fan Ventilation Control (Circle All that Apply) | Indicates Garage Exhaust Fan is Always On
vent_tc |  | Indicates Garage Exhaust Fan uses a Timeclock
vent_fc |  | Indicates Garage Exhaust Fan uses a CO with Fan Cycle
vent_vfd |  | Indicates Garage Exhaust Fan uses a CO with VFD
vent_n |  | Indicates None - There is no Garage Exhaust Fan
vent_u |  | Indicates Garage Exhaust Fan is Unknown

## Water Heat
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
waterheat_index |  | Water Heater Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
water_heater_id |  | Site-specific Unique ID
id1 | MIXED USE IDs Served? (Circle) | Indicates the Mixed Use IDs Served by the Water Heater (NOTE - NOT Space IDs - The NA column is indicated if there are no mixed use IDs)
id2
id3
id4
id5
na
water_heater_type | Water Heater Type | Indicate the water heater type using the Water Heater Type | 1 = Heat Pump 2 = DHW Tank 3 = Point of Use – Tankless or Tanks <5 gallon 4 = Dedicated Boiler 5 = HX from Space Heat Boiler 6 = Off-Site 7 = HR from Boiler equipment 8 = HR from Chiller condenser 9 = HR from Process equipment 10 = Other -1 = Unknown
water_heater_type_other |  | If other is identified, this field will be filled
fuel_type | Primary Fuel Type | Indicate the primary water heater fuel type from the Fuel Type Codes Table | 1 = Electricity 2 = Natural Gas 3 = Fuel Oil 4 = Propane 5 = Other 6 = None -1 = Unknown
fuel_type_secondary | Secondary Fuel Type | Indicate the secondary water heater fuel type from the Fuel Type Codes Table | 1 = Electricity 2 = Natural Gas 3 = Fuel Oil 4 = Propane 5 = Other 6 = None -1 = Unknown
condensing | Condensing? | Indicate whether the water heater is a condensing water heater. Condensing Water Heaters extract the additional heat from the exhaust gases to improve the overall water heater efficiency (generally above 90%). | Y = Yes N = N DK = Don't Know NF = Not Filled
number_identical_units | Number of Identical Units | The number of water heaters covered by this entry. Includes redundant units.
number_units_on_standby | Number of Redundant Units | Number of water heaters in this entry that are used strictly for backup.
age_water_heater | Age Of Water Heater (years) | Indicate the age of the water heater in years.
tank_capacity | Tank Capacity (0 if tankless) (Gallons) | The capacity of the tank water heater in gallons. Tankless water heaters of 0 gallons of capacity.
input_capacity | Input Capacity | Indicate the input capacity of the tank or tankless water heater
input_capacity_units | Input Capacity Units | kW (for electric water heaters) or MBTU (for gas water heaters). | KW, MBTU, or DK (Don't Know)
tank_insulation_wrap | External Tank Insulation? | Indicate whether there is external tank wrap insulation surrounding the water heater (tank only). | Y = Yes N = N DK = Don't Know NA = Not Applicable
additional_storage_tank | Additional Insulated Storage Tanks | Number of additional insulated storage tanks
solar_preheat | Solar Preheat? | Indicate whether the water heater uses solar energy to pre-heat building / complex water before it enters the water heater. | Y = Yes N = N DK = Don't Know NA = Not Applicable NF = Not Filled
uninsulated | Additional Un-Insulated Storage Tanks | Number of additional un-insulated storage tanks
recirculation_system | Recirculation System? | Identify whether the water heater has a recirculation system. Recirculation systems feature sensor valves that when the water on the hot water side cools to a certain temperature, recirculation the cool water back into the water heater. | Y = Yes N = N DK = Don't Know NA = Not Applicable NF = Not Filled
recirc_pump_none | If Recirculation system = yes, recirculation pump control: | Indicates there is no recirculation pump controls (runs 24/7)
recirc_pump_ems |  | Indicates EMS - Timeclock Recirculation Controls
recirc_pump_time_clock |  | Indicates Timeclock Recirculation Controls
recirc_pump_aquastat |  | Indicates Aquastat Recirculation Controls
recirc_pump_unk |  | Indicates Unknown Recirculation Controls

## Light Schedule
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
lightschedule_id |  | Light Schedule Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
seq_num |  | Site-specific Unique ID
fixture_type_id | Fixture Type ID | Site-specific Unique ID (code given by field tech)
fixture_type | Fixture Type | This is a description of the fixture type. For fixtures that would be characterized as other, the “other” can be used, or a more informative code can be used instead (e.g. Rope light or step light) Include exit lights on this page but there is no need to count them in section 10a or 11a. | See "Supplemental Lighting Codes" Tab
fixture_width | Fixture Width | Filled if Fixture type is WL - Fixture width measured in Ft. - Will be greater than 0 for Linear Fluorescents and LED Linear fixtures - Filled with 0, -1 or 1 for all other lamp types to indicate the mounting and light direction of the fixture
fixture_length | Fixture Length | Same as above, just measurement of the Length in Ft.
recessed |  | Indicates if the Fixture is recessed (not required for all fixture types)
surface_mount |  | Indicates if the Fixture is pendant mounted (not required for all fixture types)
pendant_mount |  | Indicates if the Fixture is pendant mounted (not required for all fixture types)
fixture_watts | Fixture Watts | Fixture watts
recessed_type |  | Indicates the lighting direction of an identified recessed fixture
surface_type |  | Indicates the lighting direction of an identified surface fixture
pendant_type |  | Indicates the lighting direction of an identified pendant fixture
lamp_type | Lamp Type | This is a code for the general type of lamp in the fixture. See codes and definitions in 'Supplemental Lighting Codes' Tab | See "Supplemental Lighting Codes" Tab
lamp_details | Lamp Details | This is a code for the detailed type of lamp in the fixture. See codes and definitions in 'Supplemental Lighting Codes' Tab | See "Supplemental Lighting Codes" Tab
num_lamps | # of Lamps | # of lamps per fixture or linear feet for rope lights, neon, etc.
watts_lamp | Watt/Lamp | Wattage per lamp or per linear foot for rope lights and neon. If unknown, wattages are assumed based on: 1 - wattage ranges required to be provided by surveyors in the event of an unknown wattage, or 2 - comparable fixtures in common data sources or in Section 10b, 3 - left as unknown if the fixture represents less than 2% of lighting for the building The effort spent confirming lamp wattage should correlate with the percentage of lighting represented by the lamps in the building (e.g., Surveyors should spend a more effort trying to confirm the wattage of T8s representing 90% of lighting within a site).
source | Source | Source of information for the “Watt/Lamp” & “Fixture Watts” columns. Assumed is filled for any lamps that were unknown wattages | O = Observation P = Plans I = Interview RS = Replacement Stock OM = O&M OTH = Other UNK = Unknown G = Guess A = Assumed
ballast_type | Ballast Type | Only gather if HID, T12, or T8 lamp. See codes and definitions in 'Supplemental Lighting Codes' Tab | See "Supplemental Lighting Codes" Tab
ballast_factor | Ballast Factor - If known (HP T8 ONLY) | Ballast factor is a measure of the actual lumen output for a specific lamp-ballast system relative to the rated lumen output measured with reference ballast under ANSI test conditions. Only gather for High Performance T8 lamps.
fixture_notes | Notes | Notes

## Supplemental Lighting Codes
FIXTURE TYPE CODES AND DESCRIPTIONS (use plus to the left to view - Table is grouped)
Fixture Type | Description | Detailed Description
W x L -r(d/i/b) | Recessed linear fluorescent – direct, indirect, or both (specify which). Parenthesis may be left out of suffix (e.g. “rd” rather then “r(d)”) | Recessed linear fluorescent fixture. Include width (measured – not number of lamps) and length. Mounted in ceiling. If lights the area only indirectly it’s an indirect fixture. If lights the area directly it’s a direct fixture.
W x L -s(d/i/b) | Surface Mount linear fluorescent – direct, indirect, or both (specify which) | Surface mount linear fluorescent fixture. Include width (measured – not number of lamps) and length. Mounted on the surface of the ceiling so fixture height is lower than the ceiling, typically by about 4 inches. If lights the area only indirectly it’s an indirect fixture. If lights the area directly it’s a direct fixture.
W x L –p(d/i/b) | Pendant Mount linear fluorescent – direct, indirect, or both (specify which) | Pendant mount linear fluorescent. Include width (measured – not number of lamps) and length and whether direct/indirect/both. Fixture is hanging from ceiling. If light only shines up it’s an indirect fixture. If light only shines down it’s a direct fixture.
STRIP | Bare or lensed linear fluorescent strip.
CAN | Recessed Can Fixture | Recessed can mounted in the ceiling.
DISPLAY | Miscellaneous Display Lighting | Lighting used to highlight a display or presentation space but is not track lighting.
EXIT | Exit Sign | Sign used to highlight the location of the exit for the building.
HEAD | Track Light Head | Lighting on a track potentially with multiple heads. The direction the head is pointed and the location along the track could potentially be changed.
TSK | Task Lighting | Only include for Lodging & Office building types & task lighting that is consistent throughout space. The most common type of task lighting is under-cabinet or shelf fluorescent lighting used in systems furniture. Anything that is plugged in to an outlet is basically task lighting, e.g. Torchiere fixtures.
OTH | Other | Use when the fixture type doesn’t fit into the above categories. Use of OTH is not required and is discouraged in cases where fixture is unique. Making the fixture type be descriptive (e.g. rope light, step light, down light, surface, pendant) can help keep track of the lighting during the audit and provides more information.
POLE25 | Pole Mounted Fixture | Pole <= 25’
POLE40 | Pole Mounted Fixture | Pole >25’ & <= 40’
POLE60 | Pole Mounted Fixture | Pole >40’
WALL | Wall Mounted Fixture | Wall Pack
FLOOD | Flood Light | Flood Light
Un | Unable to determine | Use when you cannot determine the fixture type.
LAMP TYPE and DETAILS CODES AND DESCRIPTIONS (use plus to the left to view - Table is grouped)
Lamp Type | Description | Lamp Details | Description | Typical Watts/Lamp
ES: Energy Savings HO: High Output LW: Low Wattage Std: Standard Wattage VHO: Very High Output
T5 | Fluorescent T5 – linear fluorescent 5/8” width. | SO | Standard Output (typical designation: F28T5, 28T5, FP28T5) | 4’ Std- 28W
2’ Std– 14W
|  | HO | High Output – Determine from model number (may have to look online). Usually designated by ‘HO’. | 2’ HO – 24W
4’ HO - 54W
4’ HO LW - 49W, 47W, or 45W
|  | Un | Unable to determine | Assume same as Standard Output
T8 | Fluorescent T8– linear fluorescent 1” width. Include T8 U shaped lamps. | SP | Standard Performance - Lumens/Watt< 90, CRI <80, Initial Lumens < 2950, Life < 20,000 hours @ 3 hour start, Lumen maintenance < 90%. | 8’ Std = 59 watts
8’ HO = 86 watts
4’ Std - 32W
4’ HO - 44 watts
2ft Std – 17W
|  | HP | High Performance – relates to the quality of the lamp: Lumens/Watt > 90, CRI >80, Initial Lumens >3100, Life > 24,000 hours @ 3 hour start, Lumen maintenance > 94%. If low wattage T8 then enter HP. If 32 watt T8, look up model number in the CEE high performance lamp list. . | 4’ Std - 32W
4’ LW -30W, 28W, 25W
|  | Un | Unable to determine | Assume same as Standard Wattage (Std).
T12 | Fluorescent T12– linear fluorescent 1.5” width. Include “U” shaped T12. | No details required | No details required | 4’ Std – 40W
4’ Std ES - 34W
4’ HO - 60W
4’ VHO – 115W
8’ Std - 75W
8’ Std ES – 60W
8’ HO - 110W
8’ HO ES – 95W
8’ VHO – 215W
8’ VHO ES – 185W
CFL | Compact Fluorescent – Include twist, twin tube, biax, triple tube and quad tube lamps. Biax/twin tube lamps can be up to 24” long. | S | Screw-in | 7W to 55W
|  | P | Pin-based
|  | Un | Unable to determine
F-OTH | Other Fluorescent – Fluorescent that doesn’t fit into one of the above categories |  | No details required EX: 4’ T10 – 40W; 5’ T17 – 90W | Varies
INC | Incandescent – very inefficient. Color most similar to natural sunlight. Common in retail. | R | Reflector –standard incandescent bulb with coating on back to direct light. Notice the shape of the bulb is more cone or pear shaped & the smooth mirror like lens. | Varies
|  | G | General Service, A type, globe, etc.
|  | D | Decorative / Miscellaneous –incandescent bulb used for decorative or misc. purpose.
|  | H-R | Halogen – Reflector - halogen bulb with coating on back to direct light. Shape of the bulb is more parabolic shaped.
|  | H-G | Halogen - General Service – more efficient than a standard incandescent due to iodine or bromide coating on tungsten filament. Notice the ‘mini’ bulb inside the larger bulb this can help identify if the bulb is a halogen or an incandescent.
|  | H-D | Halogen - Decorative / Miscellaneous –used for a halogen bulb used for decorative or misc. purpose.
|  | Un | Unable to determine.
HID | HID – High intensity discharge. Common in high bay fixtures, parking lots, and in outdoor wall and walkway lighting. CMH is used in some display situations. | MV | Mercury Vapor – very inefficient outdoor lighting, not very common, blue/green color. Sometimes preferred for landscape lighting. | Varies
|  | MH | Metal Halide - Typically used in flood lighting applications due to high output for small bulb size. Also notice the color variations in the picture; this happens as the light ages, a negative characteristic of MH. Most types are fitted with an outer glass bulb to protect the inner components and prevent heat loss. Requires a warm-up period so not used in critical areas. Common in high bay indoor applications, e.g. warehouse, factory, gym, etc. | 35W (for small installations such as flood lighting mounted on the corners of buildings) to 1000W if site lighting (high pole mounted - pictured here).
|  | CMH | Ceramic Metal Halide – The bulb contains a ceramic tube that is filled with mercury, argon, and metal halide salts. Produces a blue/white light. Smaller wattage 20-150 watts typically used in retail and driven by electronic ballast. | Same range as MH.
BALLAST TYPE CODES AND DESCRIPTIONS (use plus to the left to view - Table is grouped)
Ballast Type | Description | Detailed Description
E | Electronic – Unknown Type
SE | Standard Electronic | Driven by state of the art circuit boards. Operating Frequency 20,000Hz.25% more efficient than magnetic. Do not hum or flicker. CFLs can have integrated electronic ballasts
HPE | High Performance Electronic | Typically paired with 4’ T8 fluorescent lamps.
M | Magnetic | Driven by copper coils. Operating Frequency 60Hz.Less Efficient than Electronic. Contains Poly-chlorinated biphenyls (PCBs).
PULSE | HID Pulse Start Ballast | HID lamp which requires separate ballast to provide thousands volts to start lamp because it doesn’t contain an internal starter probe.
PROBE | HID Probe Start Ballast | HID lamp with an internal starter probe near one of the main electrodes to help in gas ionization during the first few seconds of the starting cycle.
NONE | No ballast required | Use when the lighting system requires no ballast.
Un | Unable to determine | Use if you are unable to determine what type of ballast is used.
LIGHTING FIXTURE CONTROL TYPES (use plus to the left to view - Table is grouped)
Control Type | Description | Description Details
EMS-S | Automatic Sweep Controls with EMS System | Some buildings set the controls to ‘sweep’ off all lights at night sometimes several times to get lights that have been turned back on by office or janitorial staff working late through the energy/lighting/building management system. Use this code for this case.
EMS | EMS System (without automatic sweep) | Use when there is an energy/lighting/building management system to control when the lights are turned on/off, etc. but there is NOT a programmed automatic sweep.
DS | Daylight Sensing, Details Unknown | Use when lights are dimmed based on daylighting but how the lights are dimmed is unknown. Perhaps you see photocells but no one on-site knows the details of the dimming process.
DS-SS | Daylight Sensing, Single-Step Dimming | Lamps have one reduced lighting output level, or are at max output. In general this is done by switching off a percentage of lamps with in the fixture.
DS-MN | Daylight Sensing, Multiple Stepped Dimming | Lamps have more than one reduced lighting output level, or are at max output. In general this is done by switching off a percentage of lamps with in the fixture.
DS-CD | Daylight Sensing, Continuous Dimming | Lamps can be dimmed to l a range of light levels from a min to max output.
DIM | Dimming (non-daylight) | Dimming controls which are not daylight sensing.
EGR | Egress control 24/7 | Separately controlled fixtures for emergency/egress lighting that are on 24/7. Egress lighting that is shut off to create a dark building when the building is unoccupied should not be separated or indicated as having EGR control.
MCB | Manual - circuit breaker | Lights are controlled manually at the circuit breaker or some other central switch
MS | Manual - wall switch | Lights are controlled manually at a local wall switch (full on/off).
MB | Manual - bi-level | Lights are controlled manually at a bi-level wall switch (typically two switches serve the fixtures with one switch controlling half of the lamps and the other switch controlling the remaining lamps).
OS | Occupancy Sensors | Occupancy sensors are used to turn off or reduce the light output when the space is unoccupied.
T | Timeclock (electronic or mechanical) | A timeclock turns off the lighting at a specified hour of the day and turns the lights back on at a specified hour.
OTH | Other | Controls are used but do not fit into any of these categories.
N | None (continuous) | There are no lighting controls; the lights in this space are on continuously (24/7).
Un | Unable to determine | Unable to determine if any lighting controls are used in this space.

## Lighting Summary
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
tbl_index |  | Light Summary Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
light_scheme | Briefly describe the lighting scheme (including controls) at this building. | Briefly describes the lighting design and controls at this building.
has_exterior_lighting | Does this building have exterior lighting? | Indicates if the building has exterior lighting | Y = Yes N = N DK = Don't Know NF = Not Filled
stairwell_lights | Does this building have stairwell lighting? | Indicates if the building has stairwell lighting - if yes, the next portion is filled
stairwell_none | If building has stairwell lighting, what controls are used? (circle all that apply) | None (24/7) – Stairway lighting is on 24/7. | only filled if stairwell_lights variable = Y
stairwell_off_occupied |  | Off during unoccupied – Stairway lighting is off during unoccupied hours.
stairwell_off_sensor |  | Off on occupancy sensor – Stairway lighting is switched on by occupancy sensors and off when the occupancy sensor detects no one in the space.
stairwell_on_sensor |  | Dimmed on occupancy sensor – Stairway lighting is dimmed based on occupancy sensor.
stairwell_switched |  | Switched – Stairway lighting is turned on and off using wall switches.
area_sales | Area of outdoor sales? (SF) | Area of outdoor sales area (if applicable) This is for enclosed outdoor areas such as the gardening center at the home improvement store. Do not include side walk sales displays.
egress_on | Are egress lights on all night? | Is there egress (emergency lighting) on at night? | Y = Yes N = N DK = Don't Know NA = Not Applicable NF = Not Filled
sales_lit | Are there lighting fixtures for sale that are illuminated? | Are there lighting fixtures in a lighting fixture sales department that are illuminated for demonstration purposes? Example: lighting department in the local home improvement center.
estimated_kw | If yes, Estimated Connected kW | Estimate based on # of lamps/fixtures & average wattage/lamp or wattage/fixture. Sample area if large as needed. Plans often have the display circuit capacity. | <1 kW 1-5 kW 5-20 kW 20+ kW DK = Don't Know NF = Not Filled

## Indoor Lighting
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
indoorlight_id |  | Indoor Light ID Number (Primary Key)
site_id |  | The Unique Site ID
seq_num |  | Site-specific Unique ID
space_id | Space ID | Foreign key, links to Spaces table
subspace_type | Subspace Type | Identify subspaces of interest for each Space ID. Required subspaces are identified in the sampling methodology document and lighting must be separated by these categories whether the project is sampled or not. Use code ‘Other’ or write in a descriptive subspace type when the subspace doesn’t fit into one of the below categories. See separate lighting example as a reference. | See Below
subspace_type_other | Subspace Type - Other | If Subspace type is other, specify here
sampled_subspace_area | Sampled Subspace Area (ft2) | The sampled area of the subspace. This is the sample subspace area as compared to the total subspace area in the next field
total_subspace_area | Total Subspace Area (ft2) | The total area of the subspace. If not sampling and auditing the entire subspace, this should be equal to the previous field (Sample Subspace Area).
ceiling_height | Ceiling Height | The ceiling height in the space rounded to the nearest foot.
Subspace Type/Code | Subspace Description
Aud | Auditoriums
Class | Classroom
Conf | Conference rooms
Core | Building Core/lobby/bathrooms
Corr | Corridor
Eating | Eating areas
Exam | Medical exam rooms
Groc | Grocery
Gym | Gyms
Kit | Kitchens
Lobby | Main Lobby
Mech | Mechanical Mezzanine
Off | Office
Offcl | Enclosed Office (<300sf)
Offop | Open Office
Parking | Parking Garage
Rest | Restroom/locker
Retail | Retail
Room | Patient/hotel room/Dwelling Unit
Seat | Seating Area
Show | Wholesale showrooms
Storage | Storage
Thea | Theater
Ware | Warehouses
OT - specify | Other

## Fixture Takeoff
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
fixtakeoff_id |  | Indoor Light Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
seq_num |  | Site-specific Unique ID
indoorlight_id |  | Foreign key, links to Indoor Lighting table
fixture_height | Subspace Type | The height of the fixture identified in ‘Fixture Type ID’ rounded to the nearest foot.
fixture_type_id | Subspace Type - Other | Foreign key, links (in combination with site_id) to Light Schedule table
total_fixture_count | Total Fixture Count | The total number of fixtures in the subspace or area of the subspace that is being surveyed.

## Fixture Controls
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
fixcontrols_id |  | Fixture Controls Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
seq_num |  | Site-specific Unique ID
indoorlight_id |  | Foreign key, links to Indoor Lighting table
fixtakeoff_id |  | Foreign key, links to Fixture Takeoff table
control_type | Control Type/Multiple Controls | The type of controls used on in this subspace, include all that apply, separate by a semicolon. See above control table. Do not leave this column blank. The surveyor has two options when there are different controls on the same fixture type in a space: 1. A separate entry can be made for each fixture/control type combination. Then the % lighting load controlled will be 100%. 2. One entry can be made for the fixture type and the % lighting load controlled will be something less than 100%. | See "Supplemental Lighting Codes" Tab
multiple_control_types |  | Fill if multiple controls but all control 100% of load
light_load_controlled | % Lighting load controlled | % of the lighting load that is being controlled by all the controls you listed under ‘Control Type’ For multiple controls separate by a semicolon and list in same order as ‘Control Type’.
controls_functional | Are controls overridden? | Yes/No for each type of control. For multiple controls separate by a semicolon and list in same order as ‘Control Type’.

## Outdoor Lighting
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
tbl_index |  | Outdoor Light Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
outdoorlight_id |  | Site-specific Unique ID
fixture_type_id | Fixture Type ID | Foreign key, links (in combination with site_id) to Light Schedule table
out_light_use_type | Use Type | Code that best describes the outdoor use of the lighting: • S – Used for signage (lights up text). • F – Used to directly light the building façade. This includes wall mounted down lights and flood lights directed at the façade. • P – Parking Lot: Used to light the building’s parking lot (Typically lights on poles throughout parking area). • SF – Sporting Field: Used to light a sporting field. • O – Other: Use that doesn’t fit into any of the other categories • W – Walkway/Area: Used to light the path/walkway or an area where people would congregate • ES – Exterior sales: Used to highlight items the building is selling. This is for areas indicated as exterior sales areas in the lighting section of the form. | S = Signage F = Façade P = Parking Lot SF = Sporting Field O = Other W = Walkway ES = Exterior Sales Unk = Unknown NF = Not Filled
num_fixtures | # of fixtures | The number of fixtures in the group.
out_light_control_type | Control Type | Choose the code(s) that best describes the outdoor lighting control method: • P – Photocells turn on/off lights based on available sunlight. Typically used to turn on lights in areas such as parking lots after dark. • T – A timeclock is used to turn on/off the lights based on the hour of the day. • AT – An astronomical timeclock is used to turn on/off the lights based on the hour of the day AND the date of the year. • PT – Both a photocell and a timeclock are used to turn on/off the lights. Typically used to turn on the lights in areas such as parking lots after dark, and then turn the lights off at a specified time when no one is expected to be around. Vice versa in the a.m. • M – Manual: The lights are manually controlled by a switch, circuit breaker, etc. • 24 – 24 Hour: The lights not controlled in anyway & are on 24/7. • SO – Stepped Occupancy: The lights are controlled by an occupancy sensor low level on/high level on. For example, the lights are on at low level, OS control triggers high level. • ST – Stepped Timeclock: The lights are controlled by a timeclock and are turned off/low level on/high level on. • UN – Unable to Determine: Use if you cannot determine the type of controls used. | P = Photo Cell T = Timeclock AT = Astronomical Timeclock PT = Photocell and Timeclock M = Manual 24 = 24/7 no controls SO = Stepped Occupancy ST = Stepped Timeclock UN = Unknown NF = Not Filled
out_controls_used | Are controls functional and used? | For this fixture group are the controls listed functional and used? If multiple controls are present or a percentage of the fixture controls do not work choose the answer that describes the majority of the fixtures. | Y = Yes N = N DK = Don't Know NA = Not Applicable NF = Not Filled

## Food Service Equip
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
food_index |  | Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
food_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by food service equip
sb | Kitchen Types (select all that apply | Indicates a SNACK BAR Kitchen Type | 1 indicates the presence of one of these kitchen types
ff |  | Indicates a FAST FOOD Kitchen Type
c |  | Indicates a CAFETERIA/RESTAURANT Kitchen Type
lk |  | Indicates a LARGE/COMMERCIAL KITCHEN Type
sk |  | Indicates a SMALL KITCHEN Type
ot |  | Indicates an OTHER Kitchen Type
n |  | Indicates NO KITCHEN present
total_kitchen_area | Total Kitchen Area (SQFT) (SQ FT) | Indicate the total kitchen area in square feet. Kitchen space is defined as food preparation area for any of the kitchen type categories identified above.
dining_area | Dining Area (SQFT) | Indicate the total dining area in square feet. Dining area is classified as space used to eat prepared meals.
number_meals | Number of meals served per day | Estimate the total number of meals prepared by the kitchen type areas per day. This is the essentially the number of customers. -1 is unknown
number_spray_valves | Number of pre-rinse spray valves (#) | Indicate the presence of pre-rinse spray valves. Pre-rinse spray valves are typically found in the cleaning area of the kitchen and are used to remove food particles from dishes prior to cleaning.
elec_warming_eq | Electric Warming Equipment (Yes/No) | Indicate the presence of electric food warming and holding equipment. The devices should not be used to cook / prepare food; instead they maintain the temperature of food that has already been prepared. Warming equipment would include warming drawers, and equipment used to maintain temperatures below 135 °F. | Y = Yes N = N NF = Not Filled
kitchen_hood_linear_ft | Total Linear Feet of Kitchen Hood (LF) | Indicate the total length of kitchen hood (lineal feet). Kitchen hoods remove airborne grease, combustion products, fumes, smoke, odors, heat, and steam from the air by evacuation of the air and filtration.
standard_hood_percent | Standard (% of total LF kitchen hood) | Indicate the percentage of total kitchen hood length that features standard kitchen hoods.
hr_hood_percent | HR (% of total LF kitchen hood) | Indicate the percentage of total kitchen hood length that features Heat Recovery (HR) kitchen hoods.
dcv_hood_percent | DCV (% of total LF kitchen hood) | Indicate the percentage of total kitchen hood length that features Demand Controlled Ventilation (DCV). These kitchen hoods have sensors that measure temperature, steam and smoke in the hood, and adjust the fan speed accordingly to save both fan energy and conditioned air.
compensating_hood_percent | Compensating (% of total LF kitchen hood) | Indicate the percentage of total kitchen hood length that features compensating kitchen hoods. Compensating hoods supply up to 90% make-up air through stainless steel perforated panels on the front face of the hood. The hood performs at extremely low CFM exhaust flow rates.
steamers | Steamers | Indicate the presence (None), and fuel type (Electric or Gas) of food steamers. | E = Electric G = Gas (may be Natural Gas or Propane) N = None NF = Not Filled
hot_food_cabinet | Hot Food Holding Cabinet | Indicate the presence (None), and fuel type (Electric or Gas) of hot food holding cabinets in the kitchen. Examples include any equipment used to maintain temperatures above 135 °F. (Gas may represent Propane)
boiler_fryer | Broilers / Fryers | Indicate the presence (None), and fuel type (Electric or Gas) of boilers / fryers. (Gas may represent Propane)
griddle_grill | Griddle / Grill | Indicate the presence (None), and fuel type (Electric or Gas) of griddles. (Gas may represent Propane)
combo_oven | Combination Oven | Indicate the presence (None), and fuel type (Electric or Gas) of combination oven (An oven with a combination mode. Cook in convection mode while maintaining the humidity levels you want, from 0% to 100%, reducing shrinkage and weight loss. ) (Gas may represent Propane)
oven | Oven (excluding combination ovens) | Indicate the presence (None), and fuel type (Electric or Gas) of non-combination ovens. (Gas may represent Propane)
kit_range | Range | Indicate the presence (None), and fuel type (Electric or Gas) of cooking ranges. (Gas may represent Propane)
dish_boost_fuel | Dishwasher Booster Fuel | Indicate the presence (None), and fuel type (Electric or Gas) of dishwasher booster fuel. (Gas may represent Propane)
refer_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Plug Load Refrigeration Equip
refer_vend_machines | Refrigerated Vending Machines | Indicate the number of refrigerated vending machines (e.g., fruit dispensaries).
nonrefer_vend | Non-Refrigerated Vending Machines | Indicate the number of non-refrigerated vending machines (e.g., snack dispensaries).
beverage_merch | Beverage Merchandizers (1-2 door beverage display cases) | Indicate the number of beverage merchandizers (e.g., cold soda dispensaries).
ice_machines | Ice Machines | Indicate the number of ice machines.
com_refers_full | Commercial Refrigerators (full height) (# of doors) | Indicate the total number of full height commercial refrigerator doors. Commercial refrigerators usually feature larger interior dimensions provide more storage space than their residential counterparts.
com_refers_half | Commercial Refrigerators (half height) (# of doors) | Indicate the total number of half height commercial refrigerator doors. Commercial refrigerators usually feature larger interior dimensions provide more storage space than their residential counterparts.
com_freezers | Commercial Freezers (# of doors) | Indicate the total number of commercial freezer doors. Commercial freezers usually feature larger interior dimensions provide more storage space than their residential counterparts.

## Misc Equip
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
tbl_index |  | Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
pool_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by pool/spa equip
pool_indoor | Pool Indoor (total sq. ft.) | Indicate the total indoor pool square footage.
pool_outdoor | Pool Outdoor (total sq. ft.) | Indicate the total outdoor pool square footage.
pool_fuel | Pool Fuel (Electric, Gas, Propane, Other, None) | Indicate the presence of a pool (None), and fuel type (Electric, Gas, Propane, Other). | E = Electricity NG = Natural Gas P = Propane OT = Other N = None DK = Don’t Know NF = Not Filled
hot_tub_indoor | Hot Tub Indoor (total sq. ft.) | Indicate the total indoor hot tub square footage.
hot_tub_outdoor | Hot Tub Outdoor (total sq. ft.) | Indicate the total outdoor hot tub square footage.
hot_tub_fuel | Hot Tub Fuel (Electric, Gas, Propane, Other, None) | Indicate the presence of a hot tub (None), and fuel type (Electric, Gas, Propane, Other). | E = Electricity NG = Natural Gas P = Propane OT = Other N = None DK = Don’t Know NF = Not Filled
laundry_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by laundry equip
laundry_type | Laundry Type (Coin-Op C, Drycleaner D, Small S, Large Commercial L, None N) | Type (Coin-Op C, Drycleaner D, Small S, Large Commercial L, None N) | C = Coin-Op D = Drycleaner S = Small L = Large Commercial N = None DK = Don't Know NF = Not Filled
laundry_done_onsite | % of laundry done on-site (%) | % of laundry done on-site (%)
electric_clothes_dryer | Electric Clothes Dryer (#) | Electric Clothes Dryer (#)
gas_clothes_dryer | Gas Clothes Dryer (#) | Gas Clothes Dryer (#)
lab_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by the Laboratory equip
lab_present | Laboratory Present? | Indicate the presence of a laboratory space.
specialized_lab_equip | Does this building have specialized laboratory equipment that requires extra energy consumption? | Indicate whether the surveyed building has specialized laboratory equipment that consumes additional energy? (Ex: Gas chromatographs, centrifuges, spectrometers, and analysis equipment).
fume_hood | Fume Hood (#) | Indicate the number of laboratory fume hoods.
fume_hood_control_system | Fume Hood Control System (% Variable Flow) | Indicate the percentage of laboratory fume hoods that feature a variable flow system.

## Economic Misc Equip
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
index |  | Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
hotel_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Lodging/Residential Care Additional Equipment
guest_rooms | Guest Rooms (#) (#) | Indicate the total number of guest rooms.
average_occupancy | Annual Average Occupancy (%) (%) | Indicate the annual average occupancy percentage.
inunit_cooking | Percent of rooms with in-unit cooking (%) (%) | Indicate the percentage of guest rooms with in-unit cooking.
hotel_in_unit_refer | Percent of rooms with in-unit refrigeration (%) | Indicate the percentage of guest rooms with in-unit refrigerators.
hotel_showers_present | Presence of showers | Indicate the presence of showers (Yes, No, Unknown).
hotel_low_flow_showerhead | Presence of low-flow showerheads | Indicate the presence of low flow-showerheads (Yes, No, Unknown).
health_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Healthcare Additional Equipment
surgery_rooms | Surgery Rooms (#) | Indicate the total number of surgery rooms.
beds | Beds (for overnight stay) (#) | Indicate the total number of beds for overnight stay.
high_energy_machines | High energy medical machines (#) | Indicate the total number of high energy medical machines (e.g., X-Ray machines, CT Scan, MRI machines, dialysis machines, ultrasound machines, linear accelerators, and air compressors).
office_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Office Additional Equipment
office_occupants | Occupants (#) | Indicate the number of office occupants.
laptops | Laptop PCs (#) | Indicate the number of laptop PCs.
desktops | Desktop PCs (1 computer and 1 monitor) (#) | Indicate the number of desktop PCs.
additional_monitors | Additional Monitors (#) | Indicate the number of additional monitors. In the case of a computer with two monitors, one of the monitors would be counted in this section.
printers_copiers | Printers/copiers (#) | Indicate the number of printers/copiers.
whole_or_office | Do the numbers above represent the whole building (WB) or only the office portion as specified in the lighting audit (LA)? | Specify whether the counts of office equipment represent the inventory of the entire building, or only the office portion specified in the lighting audit.
lighting_space_id | If the lighting audit area, specify representative space id. | If the counts of office equipment represent only the office portion specified in the lighting area, specify the representative space ID.
school_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by School Additional Equipment
school_classrooms | Classrooms (#) | Indicate the number of classrooms.
current_students | Current Students (#) | Indicate the number of students.
student_capacity | Student Capacity (# of seats) | Indicate the school’s student capacity.
school_fit_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Lodging/School/Fitness Additional Equipment
school_fit_showers_present | Presence of showers | Indicate the presence of showers (Yes, No, Unknown).
school_fit_low_flow_shower | Presence of low-flow showerheads | Indicate the presence of low flow-showerheads (Yes, No, Unknown).
grocery_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Additional Grocery Equipment
point_of_use_terminals | Point-of-Sale terminals (#) | Indicate the number of point-of-sale terminals in the sales area (examples include cashiers, credit card processing stations, etc.).
food_prep_meat_dept | Food Prep – Meat Dept. (1=Yes, 0=No) | Indicate the presence of a Food Prep – Meat department (1=Yes, 0=No).
food_prep_bakery | Food Prep – Bakery (1=Yes, 0=No) | Indicate the presence of a Food Prep – Bakery department (1=Yes, 0=No).
food_prep_deli | Food Prep – Deli (1=Yes, 0=No) | Indicate the presence of a Food Prep – Deli department (1=Yes, 0=No).
warehouse_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Warehouse/Grocery/Retail Additional Equipment
floor_polisher | Floor polishers (#) | Indicate the number of floor polishers.
floor_polisher_charger | Floor polisher charging stations (electric only) (#) | Indicate the number of floor polisher charging stations.
forklifts | Forklifts (electric only) (#) | Indicate the number of forklifts (for electric only).
forklift_charger | Forklift charging stations (electric only) (#) | Indicate the number of forklift charging stations (for electric only).
warehouse_air_compressors | Air Compressors (include vacuum pumps) (total HP) (total HP) | Indicate the total HP of all Air Compressors (include vacuum pumps).
all_mixed_use_id | Mixed-Use ID (s) Served | Indicate the Mixed-Use IDs served by Additional Equipment Required for ALL buildings
tvs | TVs (#) | Indicate the number of TVs.
vehicle_charging_stations | Vehicle Charging Stations (#) | Indicate the number of Charging Stations (for electric vehicles).
mech_refer_area | Area of Mechanical/Refrigeration Mezzanine (total sq. ft.) | Total Sq. Ft. of a Mechanical or Refrigeration Mezzanine.
has_refer_equip | Does this building have refrigeration equipment? | If the building has refrigeration equipment, such as Walk-Ins, Display Cases and Storage Boxes, FILL OUT SECTION 13 (refrigeration)
has_data_equip | Does this building have data center equipment? | If the building has a data center or a small room with database equipment, FILL OUT SECTION 14 (Data Center)
has_residential_areas | Does this building have Residential Areas? | Does this building have any residential areas in it? These can be Residential Floors of a mixed use building, manager’s residences at a building, or apartments that are a part of Residential Care Facilities. If YES, FILL IN SECTION 15 (Residential Areas)

## Compressor
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
NOTE: Compressor information was only collected in buildings with over 400SF of storage box and/or walk-in refrigeration, and/or more than 60LF of refrigerated display case.
comp_index |  | Compressor Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
comp_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Compressor
id2
id3
id4
id5
compressor_type | Compressor Type | Indicate the type of compressor. | R = Reciprocating SC = Screw SL =Scroll UNK = Unknown OT = Other
system_type | System Type | Use Single for condensing unit and stand-alone single compressors, and multiplex for parallel connected compressor systems. | S = Single M = Multiplex OT = Other Unk = Unknown
design_suction | Design Suction Temp | Design saturated suction temperature of the system the compressor(s) are operating at. | L = Low (0 to -40 F) M = Medium (0 to 35 F) H = High (>35 F) DK = Don't Know
manufact_model | Manufacturer & Model # (if Total HP is unknown) | Manu and model # used to ID HP later, if unknown on site.
total_hp | Total HP (per unit) | Total HP per compressor.
quantity | Quantity: | Quantity of compressors being defined.
compressor_vsd | Unloaders or VSD compressors? | Indicate the presence of compressor unloaders or compressor VSDs. Unloaders (mounted on the cylinder heads of semi-hermetic compressors) can be mechanical valves with no wire harness, or electronic controlled with wire harnesses. VSDs are mounted on the wall or on the suction group rack (could be in panel). | U = Unloader V = VSD NO/NA = Not Applicable UNK = Unknown NF = Not Filled
float_head_pres_control | Floating Head Pressure Control? | Indicated whether or not floating head pressure control is capable. | Y = Yes N = No DK = Don't Know
heat_recovery_type | Heat Recovery Type: | Indicate the type (the use) of refrigeration heat recovery (heat reclaim). Space heating (HVAC), domestic hot water (aka service water), or space heat and domestic water (both). | S = Space Heat W = DHW SD = Space Heat & DHW N = None NF = Not Filled

## Condenser
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
NOTE: Condenser information was only collected in buildings with over 400SF of storage box and/or walk-in refrigeration, and/or more than 60LF of refrigerated display case.
tbl_index |  | Condenser Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
condenser_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Condenser
id2
id3
id4
id5
idna
condenser_type | Condenser Type | Specify the type of condenser. Air-cooled are simple and most common. Air-cooled w/pre-coolers are air-cooled condensers that drawn air over a moisture source (water spray or moist pad) that is external to the condenser. Evaporative condensers draw air that is cooled by water source (internal to the condenser). Water-cooled condensers are the rarest. They can be tubing or cylinder shaped. | R = Reciprocating SC = Screw SL =Scroll UNK = Unknown OT = Other
condenser_fan_hp | Total Fan HP: (all types) | Indicate the total fan HP for the all condenser fans. | L = Low (0 to -40 F) M = Medium (0 to 35 F) H = High (>35 F) DK = Don't Know
fan_vsd | Fan VSD or multi-speed? | Indicate the presence of a condenser fan VSD or multi speed motor. This could be in the compressor room, or directly in or on a control panel mounted on the condenser. | Y = Yes N = No DK = Don't Know
fan_motor_type | Fan Motor Type | Indicate the condenser fan motor type. | SP = Shaded Pole EC = Electric Commentated PSC = Permanent Split Capacitor DK = Don't Know NA = NA NF = Not Filled
condenser_pump_hp | Pump Motor HP (evap-cooled only) | For evaporative-cooled condensers, indicate the total spray pump HP.
pump_vsd | Pump VSD? (evap-cooled only) | For evaporative-cooled condensers, indicate the presence of spray pump VSD. This could be in the compressor room, or directly in or on a control panel mounted on the condenser. | Y = Yes N = No NA = NA DK = Don't Know

## Display Cases
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
Display cases are defined as: • Self-contained or multiplex display systems accessible by customers (no stocking areas behind) • Includes open coffin cases • Examples: refrigerated display islands (open or with doors); coffin cases, aisles of refrigerated/frozen section at grocery stores
displaycases_index |  | Display Case Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
displaycases_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Refrigerated Reach-Ins
id2
id3
id4
id5
idna
idnf
display_type | Display Case Type | Specify the relative operating temperature of the case by indicating one of the three options. | MT = Medium Temp LT-FF = Low Temp Frozen Food LT-IC = Low Temp Ice Cream DK = Don't Know
self_contained | Self-Contained Compressor/Condenser? | A “Y” indicates the case in a “self-contained” unit (it has its own internal compressor and condenser). | Y = Yes N = No DK = Don't Know
case_length | Case Length: (LF) | Indicate the total linear feet of case for this case type.
cases_with_doors | Do the cases have doors? | For “reach-in” cases that have glass doors, indicate a “Y”. | Y = Yes N = No NF = Not Filled
num_doors | # of doors | Door count for this case type.
anti_sweat | Is there an Anti-sweat heater with (ASHWC) or without control (ASH)? | Indicate whether the case has anti-sweat heaters without control, with control, or no ASH present. | ASH = Anti-Sweat Heater (no controls) ASHWC = Anti-Sweat Heater with Controls NO = None NF = Not Filled DK = Don't Know
primary_light_type | Primary Lighting Type: (T12, T8, T5, LED) List lamp type, watts per lamp, and total number of lamps | Primary lighting is the predominant type of lighting found in the case. Also use this for single lighting types only. Some cases (multideck islands) have same lamp but with many lamp lengths. Record the fixture as the dominant lamp type and convert all the odd lengths to equivalents. For example, a case that has 8-4’ T5, 4-3’ T5, and 6-2’ T5 could be recorded as having 14-4’ T5 | T5, T8, T12, LED, DK or None
primary_lamp_type |  |  | Any Lamp details or notes
primary_watts_per_lamp |  |  | Watts per lamp
primary_num_lamps |  |  | Total number of lamps
secondary_light_type | Secondary Lighting Type: (T12, T8, T5, LED) List lamp type, watts per lamp, and total number of lamps | Where more than one lighting type is present in the case, use this to specify the other lighting types. | T5, T8, T12, LED, DK or None
secondary_lamp_type |  |  | Any Lamp details or notes
secondary_watts_per_lamp |  |  | Watts per lamp
secondary_num_lamps |  |  | Total number of lamps
light_schedule | Lighting Schedule (24 hours, same as store hours - SH, Occupancy Sensor – OS) | Indicate the lighting schedule for the case lights. | SH = Store Hours 24 = 24/7 Hours OS = Occupancy Sensor DK = Don’t Know NF = Not Filled

## Walk-ins
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
Walk-in/Storages Boxes are defined as: • Walk-ins are accessible by customers (refrigerated produce and beer walk-in-rooms) • Storage boxes are either exterior storage boxes or walk-ins that do not have customer access and would be mostly in the back of food service, schools, lodging, etc. (these would commonly be called walk-ins by these building types)
walkin_index |  | Walk-In Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
walkin_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Refrigerated Walk-Ins/Storage Boxes
id2
id3
id4
id5
idna
idnf
box_type | Box Type | Specify whether the refrigerated space is a walk-in or a storage box. Walk-ins are accessed by customers or worked in (as in prep rooms) by employees. Storage boxes are not meant for continuous occupancy, only temporary for restocking access by employees. | W = Refrigerated Walk-in S = Refrigerated Storage Box DK = Don't Know
temp_type | Box Temperature Type | Specify the relative operating temperature of the refrigerated space by indicating one of the three options. | MT = Medium Temp LT-FF = Low Temp Frozen Food LT-IC = Low Temp Ice Cream DK = Don't Know
location | Box Location | Indicate whether the refrigerated space is either indoor or outdoor, and conditioned. If indoor, whether or not the room the refrigerated space is in is conditioned (cooled by an HVAC system). | IC = Indoor Conditioned IU = Indoor Unconditioned O = Outdoor NF = Not Filled
floor_area | Floor Area: (SQFT) | Indicate the total floor area of the walk-in or storage box.
height | Height: (FT) | Indicate the internally measured height of the walk-in or storage box.
doorway_protection | Type of Doorway Protection? | Specify the “infiltration blocking” doorway protection devices as listed. | S = Strip curtains A = Automatic door closer N = Neither B = Both NF = Not Filled
evap_fan_controls | Evaporator fan controls? | Indicate the presence of evaporator fan controls in the refrigerate space. | Y = Yes N = No DK = Don't Know NF = Not Filled
primary_light_type | Primary Lighting Type: (T12, T8, LED, Induction, Incandescent, CFL) List lamp type, watts per lamp, and total number of lamps. | Primary lighting is the predominant type of lighting found in the walk-in or storage box. Also use this for single lighting types only. | T5, T8, T12, LED, INC, CFL, OT (Other), DK or None
primary_lamp_type |  | Any Lamp details or notes
primary_watts_per_lamp |  | Watts per lamp
primary_num_lamps |  | Total number of lamps
secondary_light_type | Secondary Lighting Type: (T12, T8, LED, Induction, Incandescent, CFL) List lamp type, watts per lamp, and total number of lamps. | Where more than one lighting type is present in the walk-in or storage box, use this to specify the second most predominant lighting type. | T5, T8, T12, LED, INC, CFL, OT (Other), DK or None
secondary_lamp_type |  | Any Lamp details or notes
secondary_watts_per_lamp |  | Watts per lamp
secondary_num_lamps |  | Total number of lamps

## Reach-ins
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
Reach-in Cases are defined as: • Refrigerated Cases that are accessible to customers AND have a walk-in area behind it used for stocking. • Example: 7-11 drink cases that are built into the wall for customer access with stocking areas behind. • Beverage Merchandizers or Commercial Refrigerators are not included in this section; the Food Service Equipment section accounts for these
reachin_index |  | Walk-In Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Refrigerated Walk-Ins/Storage Boxes
id2
id3
id4
id5
idna
idnf
reach_in_id | NA | Site-specific Unique ID
temp_type | Reach In Temperature Type | Specify the relative operating temperature of the refrigerated space by indicating one of the three options. | MT = Medium Temp LT-FF = Low Temp Frozen Food LT-IC = Low Temp Ice Cream DK = Don't Know
location | Reach-In Location | Indicate whether the refrigerated space is either indoor or outdoor, and conditioned. If indoor, whether or not the room the refrigerated space is in is conditioned (cooled by an HVAC system). | IC = Indoor Conditioned IU = Indoor Unconditioned O = Outdoor NF = Not Filled
floor_area | Floor Area: (SQFT) | Indicate the total floor area of the reach-in box.
height | Height: (FT) | Indicate the internally measured height of the reach-in box.
doors | Customer Access Doors? | Enter a “Y” to specify the presence of reach-in glass doors. If the reach-in box does not have doors, enter “N”. | Y = Yes N = No
evap_fan_controls | Evaporator fan controls? | Indicate the presence of evaporator fan controls in the refrigerate space. | Y = Yes N = No DK = Don't Know NA = Not Filled
number_doors | # of doors | If the reach-in box has doors, enter the total number. If no doors, enter zero.
front_length | Length of Reach-in Box Front (Linear FT) | Specify the total linear feet of reach-in box (the front where the doors would be or are).
primary_light_type | Primary Lighting Type: (T12, T8, LED, Induction, Incandescent, CFL) List lamp type, watts per lamp, and total number of lamps. | Primary lighting is the predominant type of lighting found in the walk-in or storage box. Also use this for single lighting types only. | T5, T8, T12, LED, INC, CFL, OT (Other), DK or None
primary_lamp_type |  | Any Lamp details or notes
primary_watts_per_lamp |  | Watts per lamp
primary_num_lamps |  | Total number of lamps
secondary_light_type | Secondary Lighting Type: (T12, T8, LED, Induction, Incandescent, CFL) List lamp type, watts per lamp, and total number of lamps. | Where more than one lighting type is present in the walk-in or storage box, use this to specify the second most predominant lighting type. | T5, T8, T12, LED, INC, CFL, OT (Other), DK or None
secondary_lamp_type |  | Any Lamp details or notes
secondary_watts_per_lamp |  | Watts per lamp
secondary_num_lamps |  | Total number of lamps

## Servers
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
server_index |  | Server Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
data_center_id |  | Site-specific Unique ID
id1 | Space IDs Served? (Circle) | Indicates the Space IDs Served by the Data Center/Server Room
id2
id3
id4
id5
total_server_floor_area | Total Floor Area: | Floor area of the server closet/server room/data center. If more than 5 data centers, total square footage is grouped
percent_space_leased | Percentage of space that is leased: | If the data center is occupied by the space owner (owner may be the tenant in a leased building), this is zero. If space in the data center is leased to an outside business (commonly referred to as co-location), the percentage that is leased is identified
integrated_telcom | Integrated with Telecomm? | Yes is indicated if the room that contains telecomm equipment as well as IT equipment is integrated
total_num_racks | Total number of racks in use | The total number of racks that are in the server room. Racks can be 2 or 4 post racks or cabinets. Racks are counted if they are 1/3 or more full.
num_racks_not_in_use | Number of racks NOT in use | Identifies the number of racks in the data center that are empty or less than 1/3 full.
total_elec_load | Total IT load (from IT contact or UPS) (kW) | The Total IT load (i.e. load serving the racks located in the data center). Collected from IT personnel or the UPS to estimate load. This is the sum of the UPS units, with detailed information on the UPS collected below. | Y = Yes N = N NF = Not Filled
ups_make | UPS Make / Model | Identifies make and model number of UPS units.
ups_capacity | UPS Capacity (kW) | Capacity of the UPS unit in kW or kVA. From nameplate or IT personnel.
ups_capacity_unit | UPS Capacity Unit | Circle kW if the units are kW or kVA if the units are kVA.
ups_load | Current UPS Load (%) | Current UPS Usage Load (%)
energy_star | Energy Star servers? | Yes or no - If any of the equipment is Energy Star
degree_virtualization | Degree of Virtualization (%) | Virtualization is the running of multiple “virtual” server loads on a single physical server. Identify if any degree of virtualization is being undertaken by the IT staff.
sep_elec_meter | Separate Electric Meter | Identifies the total electrical load of the data center is metered separately. If the meter includes IT load, distribution system losses (from transformers such as UPS units), and cooling load then ‘Y-w/HVAC’. If the data center is metered separately but does not include cooling equipment, then ‘Y-w/o HVAC’. If the data center does not have a dedicated electric meter then ‘N’.
av_elec_load | If Yes, average electric load (kW) | kW load of the meter at the time of the audit
hvac_a | HVAC description: Air cooled DX Water cooled DX Water cooled CHW Direct Evaporative cooled Indirect Evaporative cooled Building transfer / return air None | Identifies the type of cooling used to cool the data center space. All that apply are selected: Air cooled DX – Air-cooled direct-expansion computer room air conditioning unit (CRAC). DX refers to the fact that the refrigerant evaporator is in direct contact with the air stream to be cooled. Heat rejection is through air. Water cooled DX - Water-cooled direct expansion computer room air conditioning unit (CRAC). DX refers to the fact that the refrigerant evaporator is in direct contact with the air stream to be cooled. Heat rejection is through water. In water-cooled DX, a ‘fluid cooler’ is used for heat rejection, rather than an air-cooled condenser or connection to chiller coils. These systems can also include an economizer coil, where the refrigeration cycle is turned off when the glycol can be cooled below a certain temperature by the outside air. Water cooled CHW – Chiller water coils connected to computer room air handler unit for cooling air (CRAC). Direct Evaporative cooled – Unit that uses water evaporation to directly cool and humidify the air. Indirect Evaporative cooled – Unit that uses the energy from the evaporation of water to cool air through a heat exchanger device. Building transfer / return air – Building AHU return air is used to cool space. None
hvac_w_dx
hvac_w_chw
hvac_de
hvac_ie
hvac_b
hvac_n
space_temp_range | Space Temperature Range | Choose the range representing the approximate space temperature of the data center at the time of the audit.
space_humid_control | Does space have humidification control? | Yes or No. Data centers often contain humidification systems to ensure humidity requirements are maintained. CRAC units may have humidification units integral to the unit (display may indicate humidification set points).
dedicated_air_cond | Does space have dedicated air conditioning? | Yes or no. Dedicated air conditioning is a system that serves only the data center. Typical equipment types include mini split systems or DX/CRAC unit (computer room air conditioner). Examples of systems that are NOT dedicated include chilled water fan coil units where the chiller serves air handlers serving other parts of the building.
extended_hours | If NO Dedicated AC: Does data center cause building system to run extended hours? | Yes or No. If, for example, the building system is monitoring the temperature is the space and trying to maintain set point, yes would be chosen.
cooling_system_cap | If YES Dedicated AC: Total cooling system capacity (tons) | Identifies the total cooling capacity serving the data center only, in tons of cooling.
num_crac | If YES: Number of CRAC/H units (#) | Identify the total number of units:
networked | If YES: Is this equipment standalone or networked? | Yes or no - For larger data centers where there are multiple cooling units, these units may be operating based on a local controller. This may result in overcooling or situations where one unit is humidifying while the adjacent unit is dehumidifying. Network controls are used to control units as a system.
economizer | If YES: Economizer? | Yes or no - Identifies if the dedicated equipment has an air or water economizer. For example, a water-cooled DX where the unit includes waterside economizer operation.
server_hvac_condensing_type | HVAC description? | Hospitals and universities only - text description of the server room HVAC system.

## Residential Areas
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
tbl_index |  | Residential Areas Table Unique Index Number (Primary Key)
site_id |  | The Unique Site ID
res_areas_present | Residential areas present? | Yes or No - These can be Residential Floors of a mixed use building, manager’s residences at a building, or apartments that are a part of Residential Care Facilities. Generally it is defined as an area containing independent living units with a full kitchen. | will only be yes in this case and only included in the table if residential areas exist
num_res_units | Number of residential units (#) | The Number of Residential Units in the Building
res_floor_area | Floor area of residential areas (#) | The total floor area of Residential Areas (SqFt)
num_res_floors | Number of Residential Floors | The number of floors in the building that are dedicated to Residential Units
primary_heating_fuel | Primary Heating Fuel in residential areas | List Primary Heating Fuel in the residential area
res_garage_park | How many dedicated residential garage parking spaces are there? (#) | The number of parking spaces that are dedicated to the Residential Areas. | 0 for none or NA and -1 for unknown.
building_height | Is building height at or below 75 feet or over 75 | Building height estimate | <= 75ft >= 75ft Unknown
basic_res_type | Basic residential type | Indicates the type of residential space | Apartments Condo Co-op Apt & Co-op Other (specify)
basic_res_type_other |  | Filled if above is 'other'
percent_condos | What percentage of residential units are condominiums | If condo is circled in the last question, indicated the % of the residential area that are condos.
metered_separately | Is all residential and nonresidential energy use separately metered (including parking garage lighting and ventilation, elevators, HVAC and DHW systems? | Identifies if the residential areas share meters with the non-res areas of the building. | Y = Yes N = N NF = Not Filled
non_res_meters | Is all residential energy use on non-residential meters? | If some residential areas (or all) have their own meters, the next table which end uses are controlled by which meter for residential areas. | Y = Yes N = N NF = Not Filled
parking_lighting | Parking Garage Lighting | For each of the Residential End Uses to the left, indicate what meter it is on. This is only to be filled out if residential areas are not all on Non-Res meters, as indicated in the last question of the above table. SEP if the end use is on a complete separate meter, RES if it is on a residential meter separate from the commercial meter, NRES if the residential end use is on the same meter as the Non-Res and UNK if this information is unknown. | Sep = Separate Res = Residential Nres = Non-Residential Unk = Unknown
parking_vent | Parking Garage Ventilation
elevators | Elevators
hvac | HVAC
dhw | DHW
other_1 | Other End Use 1
other_2 | Other End Use 2
other_3 | Other End Use 3
other_1_specify | Other End Use 1
other_2_specify | Other End Use 2
other_3_specify | Other End Use 3

## H&U Space Info
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
site_id |  | The Unique Site ID
space_type | Hospital/University General Space Information | Indicates the type of space: (H) represents Hospital space only (U) represents University Space only (H&U) is applicable to both building types | Hospital (H) Vacant (H) Medical Office (H) Classrooms (U) Laboratory (U) Office (U) Study (U) Special Use (U) General Use (U) Support (U) Health Care (U) Residential (U) Other (H&U)
area_onsite |  | Indicates the area of each space type that is onsite
areapct_onsite |  | Indicates the percentage of each onsite space type compared to the total onsite area
area_offsite |  | Indicates the area of each space type that is offsite
areapct_offsite |  | Indicates the percentage of each offsite space type compared to the total offsite area
area_notes |  | Lists any notes about the general facility space types

## H&U HVAC
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
site_id |  | The Unique Site ID
hvac_comments | Briefly describe the HVAC system | Overall description of the HVAC system (basic configuration – include where reheat is used by type. Note any major heat recovery exhaust air, chiller, or data center.)
electric_heating_type |  | If electric heating is present, this indicates the electric heating type
central_plant_heat | Does facility have a central plant? | Indicates the uses of the central plant (heating, cooling, and/or hot water)
central_plant_cool
central_plant_servicewater
central_plant_pct_served | Percent of floor area served by central plant? | Percentage of the campus floor area served by the central plant (0-100, -1 for unknown)
reheat_energy | What kind of terminal reheat is used in central air systems? | Indicates the type of terminal reheats associated with the HVAC system, if applicable. | HW - Hot Water Elec - Electric Resistance Unk or -1 - Unknown NA - Not Applicable
sys_247 | 24/7 HVAC Operation? | Indicates the percentage of the HVAC system that runs 24/7 | Percentage Range Buckets: 0% 1-2% 3-10% 11-25% 26-50% 51-76% 76-99% All Unknown
sys_247_nightreduce | Are supply airflows of 24/7 systems reduced at night? | Indicates the percentage range of 24/7 supply airflows that are reduced at night.
sys_247_nightreduce_type |  | Identifies the type of reduction for supply airflows | Sch - Scheduled OS - Occupancy Sensored Unknown
sys_surgeryreduce | Are surgery room airflows reduced at night? | Indicates the percentage of surgery room airflows that are reduced at night. | see "Percentage Range Buckets" above
sys_surgeryreduce_type |  | Identifies the type of reduction for supply airflows | Sch - Scheduled OS - Occupancy Sensored Unknown
sys_classroom_os | What percent of classroom floor area has OS control of HVAC? | Indicates the percentage of classroom floor areas that is controlled by occupancy sensors | see "Percentage Range Buckets" above

## H&U Lighting
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
site_id |  | The Unique Site ID
light_scheme | Briefly describe the Lighting Scheme | Description of the lighting scheme (including controls) at a given facility. Notes prevalence of T12 and incandescent.
lctrl_sweep | Sweep to off control in non-24/7 areas? | Indicates the percentage of the non 24/7 floor area that utilizes an automatic sweep to control lighting
lctrl_os_office | Occupancy sensor control of lighting in the following areas? | Indicates the percentage of the office floor area that utilizes occupancy sensors | Percentage Range Buckets: None 1-20% 21-40% 41-60% 61-80% 81-99% All Unknown
lctrl_os_class |  | Indicates the percentage of the classroom floor area that utilizes occupancy sensors
lctrl_os_conf |  | Indicates the percentage of the conference room floor area that utilizes occupancy sensors
lctrl_os_storage |  | Indicates the percentage of the storage floor area that utilizes occupancy sensors
lctrl_os_restroom |  | Indicates the percentage of the restrooms floor area that utilizes occupancy sensors
lctrl_os_other |  | Indicates the percentage of an other space type floor area (defined in the next cell) that utilizes occupancy sensors
lctrl_os_type_type |  | Indicates the space type for an other space type
pct_sockets_incandescent | Percent of standard medium base screw-in sockets with incandescent lamps installed? | The percentage of incandescents that are installed in standard medium base screw-in sockets is filled listed here | 0-100% NA Unknown (-1)
active_program_t12 | Is there an active program to convert fixtures with T12 lamps? | Indicates if T12s are currently being replaced by an active program | Yes No Unk
active_program_inc | Is there an active program to convert fixtures with Incandescent lamps? | Indicates if Incandescent fixtures are currently being replaced by an active program
using_hpt8 | Are you using t8 high performance or t8 low wattage lamps? | Indicates if High Performance or Low Wattage T8s have been installed in the facility - If yes, the next four columns must be filled
pct_hpt8_32 | IF YOU HAVE 4’ T8 high performance/ low wattage lamps, approximately what percentage have the following wattage | The Percentage of HPT8s that are 32 watts | 0-100% NA Unknown (-1)
pct_hpt8_30 |  | The Percentage of HPT8s that are 30 watts
pct_hpt8_28 |  | The Percentage of HPT8s that are 28 watts
pct_hpt8_25 |  | The Percentage of HPT8s that are 25 watts
parkinggarage | Does a parking garage exist onsite? | Indicates the presence of a parking garage | Yes No Unk
pct_garage_t12 | Primary PARKING GARAGE lighting lamp types? | The percentage of lights in the parking garage that are T12 | 0-100% NA Unknown (-1)
pct_garage_t8 |  | The percentage of lights in the parking garage that are T8
pct_garage_t5 |  | The percentage of lights in the parking garage that are T5
pct_garage_hid |  | The percentage of lights in the parking garage that are HID
pct_garage_led |  | The percentage of lights in the parking garage that are LED
pct_garage_other |  | The percentage of lights in the parking garage that are 'other'
garage_other |  | Indicates the 'other' lighting type if the above is filled
pct_garage_unknown |  | The percentage of lights in the parking garage that are LED
parkinglot | Primary PARKING LOT / ROADWAY lighting lamp types? | Indicates the presence of a parking lot/roadway lighting | Yes No Unk
pct_parklot_hid | Primary PARKING LOT / ROADWAY lighting lamp types? | The percentage of parking lot/roadway lighting that are HID | 0-100% NA Unknown (-1)
pct_parklot_led |  | The percentage of parking lot/roadway lighting that are LED
pct_parklot_other |  | The percentage of parking lot/roadway lighting that are other
pct_parklot_unknown |  | The percentage of parking lot/roadway lighting that are unknown
notes_page5 |  | Any notes on the lighting given

## H&U Misc
DB Variable Name | Survey Form Field/Question | Description | Table of Codes (if necessary)
site_id |  | Table Unique Index Number (Primary Key)
area_offsite_owned | Off-site floor area associated with campus - owned and operated? (ft2) | The total area of offsite floor area that is owned
area_offsite_leased | Off-site floor area associated with campus - leased and operated? (ft2) | The total area of offsite floor area that is owned
pct_built_after_2003 | Percent of facility floor area built in 2004 or after? | The percentage of the floor area that was build after 2003
pct_built_before_1960 | Percent of facility floor area built before 1960? | The percentage of the floor area that was build before 1960
area_next2yrs | Amount of floor are coming on-line in next 2 years? | The total floor are coming on-line in the next 2 years (ft2, 0 if none, -1 if yes but unknown amount)
change_next2yrs | Are there other changes planned for the next 2 years that will have large impact on energy use? | Indicates if any changes are planned in the next two years that will significantly impact energy use | Yes No Unk
change_next2yrs_comment | If yes, describe: | Describes the expected changes
area_last3yrs | Amount of floor came on-line in last 3 years? | The total floor are that came on-line in the last 3 years (ft2, 0 if none, -1 if yes but unknown amount)
change_last3yrs | Have there been major changes in the last 3 years that impact energy use? | Indicates if any changes in the past 3 years significantly impacted energy use | Yes No Unk
change_last3yrs_comment | If yes, describe: | Describes the major changes in energy use of the last 3 years
conservation_plan | Is there an energy conservation plan, or list of potential conservation measures for the facility? | Indicates if there is an energy conservation plan or list of potential conservation measures for the facility | Yes No Unk
ownership_type | Ownership type | Indicates the Ownership type (Non-profit, Profit, Governmental, Public, Private, Other) | NP - Non-Profit G - Governmental Pub - Public Pri - Private Oth - Other
employee_fte | Employees (FTE #) | Number of Full Time Employees | Hospital Only
trauma_level | Trauma Center Level (1-5, 0 for none) | Indicates the level of Trauma Center Care
tertiary_care | Offers Tertiary Care? | Indicates if the Hospital offers tertiary care
beds_licensed | Bed – Licenses (for overnight stay) | The number of overnight licensed beds
beds_avg_occ | Average Occupancy | Average occupancy of overnight beds
assisted_care_rooms | Number of assisted care rooms? | Number of assisted care rooms
assisted_care_rooms_notes |  | Notes associated with assisted care rooms
current_students_undergrad | Current undergraduate students | Number of undergraduate students | University Only
current_students_grad | Current graduate students | Number of graduate students
current_students_professional | Current professional students | Number of professional students
dorm_rooms | Student Housing on campus: number of rooms | Number of Dorm Rooms or other on-campus housing units
dorm_residents | Student Housing on campus: number of residents | Number of student residents
fte_academic | Academic FTE | Number of full time academic employees
fte_non_academic | Non - Academic FTE | Number of full time non-academic employees
park_lot_.area |  | Parking Lot Area
park_garage_spaces |  | Number of Parking Garage Spaces (to differentiate from parking spaces in building information)
other_type |  | Provides a description of any "other" fuel types found onsite
notes_page1 |  | General Building and Usage Notes
notes_page2_OM |  | Occupancy and Management Notes
notes_page3_areas |  | Space\Functional Use Area Notes
notes_page4 |  | Energy Sources/HVAC Notes
notes_page6 |  | Data Center Notes